## Contents
Elia Adequacy Report - study assumptions
Need for strategic reserve for the winter 2021-22
This data is provided in the framework of the evaluation of the strategic reserve volume for winter 2021-22
It includes forecasts for the 3 next winters 2021-22, 2022-23 and 2023-2024.
1. Production
1.1 Production summary
1.2 Individually modelled thermal production
1.3 Renewable production
1.4 Storage
1.5 Profiled thermal production
1.6 Forced outage rates
2. Consumption
2.1 Demand
2.2 Demand profile
2.3 Market response
3. Balancing reserves
4. Flow based domains

## 1.1 Production summary
1.1 Production summary
Production capacity for winter [MW]
Production type |  | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24
Individually modelled non renewable thermal production |  | 11752.1 | 11752.1 | 11784.1 | 10760.1 | 9734.1
CCGT/GT/CL | Gas | 4912 | 4912 | 4912 | 4912 | 4912
CHP | Gas | 739.1 | 739.1 | 771.1 | 771.1 | 771.1
| Nuclear | 5943 | 5943 | 5943 | 4937 | 3929
| Oil | 158 | 158 | 158 | 140 | 122
| Coal | 0 | 0 | 0 | 0 | 0
Profiled thermal non renewable production |  | 1206 | 1297 | 1379 | 1379 | 1379
Renewable production |  | 9184.9 | 10802.349 | 12198.0852 | 12910.8903 | 13593.9553
| Wind | 3408.9 | 4345 | 5212.95 | 5380.95 | 5545.95
| Photovoltaics | 4550 | 5254.149 | 5816.5773 | 6372.3677 | 6922.5405
| Hydro RoR | 117 | 117 | 121 | 125 | 129
| Biomass - individually modelled | 348 | 273 | 273 | 273 | 273
| Biomass - profiled | 446 | 503.2 | 464.5578 | 427.1726 | 391.0648
| Waste - individually modelled | 264 | 264 | 264 | 286.4 | 286.4
| Waste - profiled | 51 | 46 | 46 | 46 | 46
Pumped storage |  | 1224 | 1224 | 1224 | 1224 | 1224
Green cells indicate a change in assumptions

## 1.2 Ind. mod. thermal prod.
1.2 Individually modelled thermal production
Owner | Production unit name | Type | Fuel type | Production capacity [MW] | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | Comment
Engie electrabel | Syral Aalst GT | CHP | Gas | 43 | yes | yes | yes | yes | yes
Engie electrabel | Syral Aalst ST | CHP | Gas | 5 | yes | yes | yes | yes | yes
Engie electrabel | AALTER TJ | TJ | Oil | 18 | yes | yes | yes | yes | yes | [1]
Engie electrabel | AMERCOEUR 1R GT | CCGT-GT | Gas | 289 | yes | yes | yes | yes | yes
Engie electrabel | AMERCOEUR 1R ST_cur | CCGT-ST | Gas | 162 | yes | yes | yes | yes | yes
Luminus | EDF Luminus Angleur GT41 | GT | Gas | 64 | yes | yes | yes | yes | yes
Luminus | EDF Luminus Angleur GT42 | GT | Gas | 64 | yes | yes | yes | yes | yes
Luminus | EDF Luminus Angleur GT31 | CCGT-GT | Gas | 25 | yes | yes | yes | yes | yes
Luminus | EDF Luminus Angleur GT32 | CCGT-GT | Gas | 25 | yes | yes | yes | yes | yes
Engie electrabel | AWIRS 4 | CL | Biomass | 75 | yes | no | no | no | no
Engie electrabel | BEERSE TJ | TJ | Oil | 32 | yes | yes | yes | yes | yes | [1]
Indaver | Beveren 2 Indaver | IS | Waste | 21 | yes | yes | yes | yes | yes
Engie electrabel | Beveren Ineos Phenol Chem | CHP | Gas | 25.1 | yes | yes | yes | yes | yes
Indaver | Beveren Sleco | IS | Waste | 41 | yes | yes | yes | yes | yes
Biostoom | Biostoom Oostende | IS | Waste | 19.4 | yes | yes | yes | yes | yes
Engie electrabel | CIERREUX TJ | TJ | Oil | 18 | yes | yes | yes | yes | yes | [1]
Engie electrabel | DOEL 1 | NU | Nuclear | 445 | yes | yes | yes | yes | yes
Engie electrabel | DOEL 2 | NU | Nuclear | 445 | yes | yes | yes | yes | yes
Engie electrabel | DOEL 3 | NU | Nuclear | 1006 | yes | yes | yes | no | no | Decommissiong foreseen as by law from 01/10/2022
Engie electrabel | DOEL 4 | NU | Nuclear | 1039 | yes | yes | yes | yes | yes
Engie electrabel | DROGENBOS GT1 | CCGT-GT | Gas | 150 | yes | yes | yes | yes | yes
Engie electrabel | DROGENBOS GT2 | CCGT-GT | Gas | 150 | yes | yes | yes | yes | yes
Engie electrabel | DROGENBOS ST | CCGT-ST | Gas | 160 | yes | yes | yes | yes | yes
Euro-silo | Euro-Silo | CHP | Gas | 12.9 | yes | yes | yes | yes | yes
Green Power | Greenpower Oostende | CHP | Waste | 20 | yes | yes | yes | yes | yes
Luminus | EDF Luminus Ham GT31 | GT | Gas | 58 | yes | yes | yes | yes | yes
Luminus | EDF Luminus Ham GT32 | GT | Gas | 58 | yes | yes | yes | yes | yes
Luminus | EDF Luminus Ham STEG | CCGT | Gas | 39 | yes | yes | yes | yes | yes
Engie electrabel | HERDERSBRUG GT1 | CCGT-GT | Gas | 157 | yes | yes | yes | yes | yes
Engie electrabel | HERDERSBRUG GT2 | CCGT-GT | Gas | 156.3 | yes | yes | yes | yes | yes
Engie electrabel | HERDERSBRUG ST | CCGT-ST | Gas | 167 | yes | yes | yes | yes | yes
IPALLE | Ipalle Thumaide | IS | Waste | 34 | yes | yes | yes | yes | yes
Indaver | Beveren 3 Indaver | IS | Waste | 24 | yes | yes | yes | yes | yes
INEOS | INESCO GT1 | CHP | Gas | 44.8 | yes | yes | yes | yes | yes
INEOS | INESCO GT2 | CHP | Gas | 44.8 | yes | yes | yes | yes | yes
INEOS | INESCO ST | CHP | Gas | 48.5 | yes | yes | yes | yes | yes
INTRADEL | Intradel Herstal IS | IS | Waste | 32 | yes | yes | yes | yes | yes
IVBO | IVBO | IS | Waste | 16 | yes | yes | yes | yes | yes
Luminus | IZEGEM | CHP | Gas | 20 | yes | yes | yes | yes | yes
Inovyn | Jemeppe-sur-Sambre GT1 | CCGT-GT | Gas | 48 | yes | yes | yes | yes | yes
Inovyn | Jemeppe-sur-Sambre GT2 | CCGT-GT | Gas | 48 | yes | yes | yes | yes | yes
Inovyn | Jemeppe-sur-Sambre ST | CCGT-ST | Gas | 10 | yes | yes | yes | yes | yes
Engie electrabel | Sappi Lanaken GT | CHP | Gas | 43 | yes | yes | yes | yes | yes
STORA | STORA LANGERBRUGGE WKK1 | CHP | Biomass | 10 | yes | yes | yes | yes | yes
STORA | STORA LANGERBRUGGE WKK2 | CHP | Biomass | 40 | yes | yes | yes | yes | yes
Lillo Energy | Lillo Degussa GT1 | CHP | Gas | 43 | yes | yes | yes | yes | yes
Lillo Energy | Lillo Degussa GT2 | CHP | Gas | 32 | yes | yes | yes | yes | yes
Lillo Energy | Lillo Degussa ST | CHP | Gas | 10 | yes | yes | yes | yes | yes
Direct Energie | Marcinelle Energie TGV | CCGT | Gas | 413 | yes | yes | yes | yes | yes
Engie electrabel | Oorderen Bayer | CL | Steam | 43 | yes | yes | yes | yes | yes
Engie electrabel | Monsanto Lillo WKK EBL | CL | Steam | 43 | yes | yes | yes | yes | yes
Luminus | EDF Luminus Ringvaart STEG | CCGT | Gas | 385 | yes | yes | yes | yes | yes
Engie electrabel | RODENHUIZE 4 | CL | Biomass | 205 | yes | yes | yes | yes | yes
Engie electrabel | SAINT-GHISLAIN STEG_cur | CCGT | Gas | 350 | yes | yes | yes | yes | yes
EXXONMOBIL | Scheldelaan Exxonmobil | CHP | Gas | 140 | yes | yes | yes | yes | yes
Luminus | EDF Luminus Seraing GT1 | CCGT-GT | Gas | 150 | yes | yes | yes | yes | yes
Luminus | EDF Luminus Seraing GT2 | CCGT-GT | Gas | 150 | yes | yes | yes | yes | yes
Luminus | EDF Luminus Seraing TGV | CCGT-ST | Gas | 170 | yes | yes | yes | yes | yes
TAMINCO | TAMINCO Gent WKK | CCGT-ST | Gas | 6.3 | yes | yes | yes | yes | yes
Engie electrabel | TIHANGE 1N | NU | Nuclear | 481 | yes | yes | yes | yes | yes
Engie electrabel | TIHANGE 1S | NU | Nuclear | 481 | yes | yes | yes | yes | yes
Engie electrabel | TIHANGE 2 | NU | Nuclear | 1008 | yes | yes | yes | no | no | Decommissiong foreseen as by law from 01/02/2023
Engie electrabel | TIHANGE 3 | NU | Nuclear | 1038 | yes | yes | yes | yes | yes
T-Power | T-Power | CCGT | Gas | 425 | yes | yes | yes | yes | yes
Engie electrabel | Vilvoorde GT | CCGT-GT | Gas | 255 | yes | yes | yes | yes | yes
Engie electrabel | Vilvoorde ST | CCGT-ST | Gas | 121 | no | no | no | no | no
TOTAL | Wilmarsdonk Total GT1 | CHP | Gas | 43 | yes | yes | yes | yes | yes
TOTAL | Wilmarsdonk Total GT2 | CHP | Gas | 43 | yes | yes | yes | yes | yes
TOTAL | Wilmarsdonk Total GT3 | CHP | Gas | 43 | yes | yes | yes | yes | yes
Zandvliet Power NV | Zandvliet Power | CCGT | Gas | 386.2 | yes | yes | yes | yes | yes
Engie electrabel | Zedelgem TJ | TJ | Oil | 18 | yes | yes | yes | yes | yes | [1]
Engie electrabel | Fluxys LNG Zeebrugge WKK | CHP | Gas | 40 | yes | yes | yes | yes | yes
Engie electrabel | Zeebrugge TJ | TJ | Oil | 18 | yes | yes | yes | yes | yes | [1]
Engie electrabel | Zelzate 2 Knippegroen | CCGT | Gas | 305 | yes | yes | yes | yes | yes
Engie electrabel | Zelzate TJ | TJ | Oil | 18 | yes | yes | yes | yes | yes | [1]
Engie electrabel | Zwijndrecht Lanxess GT | CHP | Gas | 43 | yes | yes | yes | yes | yes
Engie electrabel | Zwijndrecht Lanxess ST | CHP | Gas | 15 | yes | yes | yes | yes | yes
Engie electrabel | ISVAG | IS | Waste | 12 | yes | yes | yes | yes | yes
Engie electrabel | NOORDSCHOTE TJ | TJ | Oil | 18 | yes | yes | yes | yes | yes | [1]
Engie electrabel | SCHAERBEEK SIOMAB ST1 | IS | Waste | 15 | yes | yes | yes | yes | yes
Engie electrabel | SCHAERBEEK SIOMAB ST2 | IS | Waste | 15 | yes | yes | yes | yes | yes
Engie electrabel | SCHAERBEEK SIOMAB ST3 | IS | Waste | 15 | yes | yes | yes | yes | yes
Biopower | Biomassa Oostende | IS | Biomass | 18 | yes | yes | yes | yes | yes
Engie electrabel | TURBOJET VOLTA | TJ | Oil | 18 | yes | yes | yes | yes | yes | [1]
Borealis | Borealis Kallo Cogen GT_ST | CHP | Gas | 32 | no | no | yes | yes | yes
Indaver | E-wood | IS | Waste | 22 | no | no | no | yes | yes | Input regions: should be comissioned in 2022
Legend Unit-Type
CCGT | Combined Cycle
CCGT-GT | Combined Cycle - Gas Turbine
CCGT-ST | Combined Cycle - Steam Turbine
CL | Classic
GT | Gas Turbine
ST | Steam Turbine
IS | Incineration Station
NU | Nuclear
TJ | TurboJet
CHP | Cogeneration Unit
[1] A decreasing trend is foreseen due to the aging of the assets see sheet 1.1 production summary

## 1.3 Renewable prod.
1.3 Renewable production
Production capacity in winter [MW]
Production type |  | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24
Wind
| onshore | 2223 | 2789 | 2960 | 3128 | 3293
| offshore | 1556 | 2252.95 | 2252.95 | 2252.95 | 2252.95
Photovoltaics |  | 4550 | 5254.149 | 5816.5773 | 6372.3677 | 6922.5405
Biofuel |  | 794 | 776.2 | 737.5578 | 700.1726 | 664.0648
| individually modelled | 348 | 273 | 273 | 273 | 273
| profiled | 446 | 503.2 | 464.5578 | 427.1726 | 391.0648
Waste |  | 319 | 314 | 314 | 314 | 314
| individually modelled | 264 | 264 | 264 | 286 | 286
| profiled | 51 | 46 | 46 | 46 | 46
Hydro - run of river |  | 117 | 117 | 121 | 125 | 129
For onshore capacity the projections of the 3 regions were consulted.
For solar capacity the projections of the 3 regions were consulted.
For offshore capacity the commissioning dates of the wind farms were consulted.
For Biofuel & Waste CIPU the latest known information of plant owners is taken into account.
For Biofuel non CIPU the capacities from the Elia PISA database are combined with the growth rates projected in the PNEC scenario WAM.
For Waste non CIPU the capacities from the Elia PISA database are consulted and deemed to remain constant.
For hydro capacity the projections of the 3 regions were consulted.

## 1.4 Storage
Storage
BE storage facilities
|  |  | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24
Pumped storage
| Capacity [MW] | Pumped-storage | 1224 | 1224 | 1224 | 1224 | 1224
| Reservoir volume [MWh] | Storage reservoir | 5800 | 5800 | 5800 | 5800 | 5800
|  | Available storage for economical dispatch | 5300 | 5300 | 5300 | 5300 | 5300
Other storage facilities
| Total capacity [MW] |  | 25.6 | 26 | 131.0829 | 219 | 358
|  | Large scale storage | 26 | 26 | 72 | 97 | 171
| Capacity [MW] | Small scale storage | 0 | 0 | 29.0829 | 60.9447 | 95.5574
|  | Vehicule-to-grid | 0 | 0 | 30 | 61 | 91
|  | Large scale storage | 26 | 26 | 72 | 97 | 171
| Reservoir volume [MWh] | Small scale storage | 0 | 0 | 87.2487 | 182.8342 | 286.6723
|  | Vehicule-to-grid | 0 | 0 | 120 | 240 | 360
Large scale storage estimations are based on projects that are at least under study and known by Elia.
Small scale storage estimations are based on the assumption that each year 0.5% of the PV installations add a battery capacity of the size of the PV installation (with 3 hours storage) as from winter 2021-22
Vehicule-to-grid estimations are based on the assumption that each year 1% of the new EV registrations will be capable of providing V2G services to the grid at any time assuming a charger of 7kW and a storage of 4 hours

## 1.5 Profiled thermal production
1.5 Profiled thermal production
Profiled production capacity in winter [MW]
Fuel type | 2019-20 | 2020-21 | 2021-2022 | 2022-2023 | 2023-2024
Waste | 51 | 46 | 46 | 46 | 46
Biomass | 446 | 503.2 | 464.5578 | 427.1726 | 391.0648
Gas and other | 1206 | 1297 | 1379 | 1379 | 1379
Normalised hourly production
[% of profiled production capacity]
Date | Hour |  | Waste + Biosmass + Gas-fired + Other
2021-11-01 | 44501 |  | 48.39%
2021-11-01 01:00 | 44501.0417 |  | 48.94%
2021-11-01 02:00 | 44501.0833 |  | 47.77%
2021-11-01 03:00 | 44501.125 |  | 47.33%
2021-11-01 04:00 | 44501.1667 |  | 47.08%
2021-11-01 05:00 | 44501.2083 |  | 47.6%
2021-11-01 06:00 | 44501.25 |  | 49.69%
2021-11-01 07:00 | 44501.2917 |  | 53.5%
2021-11-01 08:00 | 44501.3333 |  | 55.51%
2021-11-01 09:00 | 44501.375 |  | 56.36%
2021-11-01 10:00 | 44501.4167 |  | 56.28%
2021-11-01 11:00 | 44501.4583 |  | 56.03%
2021-11-01 12:00 | 44501.5 |  | 56.54%
2021-11-01 13:00 | 44501.5417 |  | 56.49%
2021-11-01 14:00 | 44501.5833 |  | 56.35%
2021-11-01 15:00 | 44501.625 |  | 56.23%
2021-11-01 16:00 | 44501.6667 |  | 56.07%
2021-11-01 17:00 | 44501.7083 |  | 56.09%
2021-11-01 18:00 | 44501.75 |  | 56.81%
2021-11-01 19:00 | 44501.7917 |  | 55.79%
2021-11-01 20:00 | 44501.8333 |  | 54.23%
2021-11-01 21:00 | 44501.875 |  | 52.63%
2021-11-01 22:00 | 44501.9167 |  | 50.92%
2021-11-01 23:00 | 44501.9583 |  | 50.3%
2021-11-02 | 44502 |  | 51.4%
2021-11-02 01:00 | 44502.0417 |  | 50.71%
2021-11-02 02:00 | 44502.0833 |  | 50.67%
2021-11-02 03:00 | 44502.125 |  | 50.97%
2021-11-02 04:00 | 44502.1667 |  | 51.32%
2021-11-02 05:00 | 44502.2083 |  | 51.98%
2021-11-02 06:00 | 44502.25 |  | 54.71%
2021-11-02 07:00 | 44502.2917 |  | 58.74%
2021-11-02 08:00 | 44502.3333 |  | 59.21%
2021-11-02 09:00 | 44502.375 |  | 58.84%
2021-11-02 10:00 | 44502.4167 |  | 58.45%
2021-11-02 11:00 | 44502.4583 |  | 58.39%
2021-11-02 12:00 | 44502.5 |  | 58.31%
2021-11-02 13:00 | 44502.5417 |  | 58.27%
2021-11-02 14:00 | 44502.5833 |  | 58.66%
2021-11-02 15:00 | 44502.625 |  | 58.87%
2021-11-02 16:00 | 44502.6667 |  | 59.25%
2021-11-02 17:00 | 44502.7083 |  | 59.63%
2021-11-02 18:00 | 44502.75 |  | 60.38%
2021-11-02 19:00 | 44502.7917 |  | 59.46%
2021-11-02 20:00 | 44502.8333 |  | 58.26%
2021-11-02 21:00 | 44502.875 |  | 57%
2021-11-02 22:00 | 44502.9167 |  | 55.77%
2021-11-02 23:00 | 44502.9583 |  | 54.98%
2021-11-03 | 44503 |  | 51.54%
2021-11-03 01:00 | 44503.0417 |  | 50.85%
2021-11-03 02:00 | 44503.0833 |  | 50.81%
2021-11-03 03:00 | 44503.125 |  | 51.11%
2021-11-03 04:00 | 44503.1667 |  | 51.46%
2021-11-03 05:00 | 44503.2083 |  | 52.13%
2021-11-03 06:00 | 44503.25 |  | 54.87%
2021-11-03 07:00 | 44503.2917 |  | 58.91%
2021-11-03 08:00 | 44503.3333 |  | 59.37%
2021-11-03 09:00 | 44503.375 |  | 59%
2021-11-03 10:00 | 44503.4167 |  | 58.62%
2021-11-03 11:00 | 44503.4583 |  | 58.55%
2021-11-03 12:00 | 44503.5 |  | 58.47%
2021-11-03 13:00 | 44503.5417 |  | 58.44%
2021-11-03 14:00 | 44503.5833 |  | 58.82%
2021-11-03 15:00 | 44503.625 |  | 59.04%
2021-11-03 16:00 | 44503.6667 |  | 59.41%
2021-11-03 17:00 | 44503.7083 |  | 59.79%
2021-11-03 18:00 | 44503.75 |  | 60.55%
2021-11-03 19:00 | 44503.7917 |  | 59.63%
2021-11-03 20:00 | 44503.8333 |  | 58.42%
2021-11-03 21:00 | 44503.875 |  | 57.16%
2021-11-03 22:00 | 44503.9167 |  | 55.92%
2021-11-03 23:00 | 44503.9583 |  | 55.14%
2021-11-04 | 44504 |  | 51.2%
2021-11-04 01:00 | 44504.0417 |  | 50.52%
2021-11-04 02:00 | 44504.0833 |  | 50.48%
2021-11-04 03:00 | 44504.125 |  | 50.77%
2021-11-04 04:00 | 44504.1667 |  | 51.12%
2021-11-04 05:00 | 44504.2083 |  | 51.79%
2021-11-04 06:00 | 44504.25 |  | 54.51%
2021-11-04 07:00 | 44504.2917 |  | 58.52%
2021-11-04 08:00 | 44504.3333 |  | 58.98%
2021-11-04 09:00 | 44504.375 |  | 58.61%
2021-11-04 10:00 | 44504.4167 |  | 58.23%
2021-11-04 11:00 | 44504.4583 |  | 58.17%
2021-11-04 12:00 | 44504.5 |  | 58.09%
2021-11-04 13:00 | 44504.5417 |  | 58.05%
2021-11-04 14:00 | 44504.5833 |  | 58.44%
2021-11-04 15:00 | 44504.625 |  | 58.65%
2021-11-04 16:00 | 44504.6667 |  | 59.02%
2021-11-04 17:00 | 44504.7083 |  | 59.4%
2021-11-04 18:00 | 44504.75 |  | 60.15%
2021-11-04 19:00 | 44504.7917 |  | 59.24%
2021-11-04 20:00 | 44504.8333 |  | 58.04%
2021-11-04 21:00 | 44504.875 |  | 56.79%
2021-11-04 22:00 | 44504.9167 |  | 55.56%
2021-11-04 23:00 | 44504.9583 |  | 54.78%
2021-11-05 | 44505 |  | 51.27%
2021-11-05 01:00 | 44505.0417 |  | 50.59%
2021-11-05 02:00 | 44505.0833 |  | 50.55%
2021-11-05 03:00 | 44505.125 |  | 50.84%
2021-11-05 04:00 | 44505.1667 |  | 51.19%
2021-11-05 05:00 | 44505.2083 |  | 51.86%
2021-11-05 06:00 | 44505.25 |  | 54.58%
2021-11-05 07:00 | 44505.2917 |  | 58.6%
2021-11-05 08:00 | 44505.3333 |  | 59.06%
2021-11-05 09:00 | 44505.375 |  | 58.69%
2021-11-05 10:00 | 44505.4167 |  | 58.31%
2021-11-05 11:00 | 44505.4583 |  | 58.25%
2021-11-05 12:00 | 44505.5 |  | 58.17%
2021-11-05 13:00 | 44505.5417 |  | 58.13%
2021-11-05 14:00 | 44505.5833 |  | 58.51%
2021-11-05 15:00 | 44505.625 |  | 58.73%
2021-11-05 16:00 | 44505.6667 |  | 59.1%
2021-11-05 17:00 | 44505.7083 |  | 59.48%
2021-11-05 18:00 | 44505.75 |  | 60.23%
2021-11-05 19:00 | 44505.7917 |  | 59.32%
2021-11-05 20:00 | 44505.8333 |  | 58.12%
2021-11-05 21:00 | 44505.875 |  | 56.86%
2021-11-05 22:00 | 44505.9167 |  | 55.63%
2021-11-05 23:00 | 44505.9583 |  | 54.85%
2021-11-06 | 44506 |  | 49.48%
2021-11-06 01:00 | 44506.0417 |  | 50.05%
2021-11-06 02:00 | 44506.0833 |  | 48.85%
2021-11-06 03:00 | 44506.125 |  | 48.4%
2021-11-06 04:00 | 44506.1667 |  | 48.15%
2021-11-06 05:00 | 44506.2083 |  | 48.68%
2021-11-06 06:00 | 44506.25 |  | 50.82%
2021-11-06 07:00 | 44506.2917 |  | 54.71%
2021-11-06 08:00 | 44506.3333 |  | 56.77%
2021-11-06 09:00 | 44506.375 |  | 57.64%
2021-11-06 10:00 | 44506.4167 |  | 57.56%
2021-11-06 11:00 | 44506.4583 |  | 57.3%
2021-11-06 12:00 | 44506.5 |  | 57.82%
2021-11-06 13:00 | 44506.5417 |  | 57.77%
2021-11-06 14:00 | 44506.5833 |  | 57.62%
2021-11-06 15:00 | 44506.625 |  | 57.51%
2021-11-06 16:00 | 44506.6667 |  | 57.34%
2021-11-06 17:00 | 44506.7083 |  | 57.36%
2021-11-06 18:00 | 44506.75 |  | 58.1%
2021-11-06 19:00 | 44506.7917 |  | 57.06%
2021-11-06 20:00 | 44506.8333 |  | 55.46%
2021-11-06 21:00 | 44506.875 |  | 53.82%
2021-11-06 22:00 | 44506.9167 |  | 52.07%
2021-11-06 23:00 | 44506.9583 |  | 51.43%
2021-11-07 | 44507 |  | 49.62%
2021-11-07 01:00 | 44507.0417 |  | 50.18%
2021-11-07 02:00 | 44507.0833 |  | 48.98%
2021-11-07 03:00 | 44507.125 |  | 48.53%
2021-11-07 04:00 | 44507.1667 |  | 48.28%
2021-11-07 05:00 | 44507.2083 |  | 48.81%
2021-11-07 06:00 | 44507.25 |  | 50.95%
2021-11-07 07:00 | 44507.2917 |  | 54.85%
2021-11-07 08:00 | 44507.3333 |  | 56.92%
2021-11-07 09:00 | 44507.375 |  | 57.79%
2021-11-07 10:00 | 44507.4167 |  | 57.71%
2021-11-07 11:00 | 44507.4583 |  | 57.45%
2021-11-07 12:00 | 44507.5 |  | 57.98%
2021-11-07 13:00 | 44507.5417 |  | 57.92%
2021-11-07 14:00 | 44507.5833 |  | 57.78%
2021-11-07 15:00 | 44507.625 |  | 57.66%
2021-11-07 16:00 | 44507.6667 |  | 57.5%
2021-11-07 17:00 | 44507.7083 |  | 57.51%
2021-11-07 18:00 | 44507.75 |  | 58.26%
2021-11-07 19:00 | 44507.7917 |  | 57.21%
2021-11-07 20:00 | 44507.8333 |  | 55.6%
2021-11-07 21:00 | 44507.875 |  | 53.96%
2021-11-07 22:00 | 44507.9167 |  | 52.21%
2021-11-07 23:00 | 44507.9583 |  | 51.57%
2021-11-08 | 44508 |  | 51.82%
2021-11-08 01:00 | 44508.0417 |  | 51.12%
2021-11-08 02:00 | 44508.0833 |  | 51.08%
2021-11-08 03:00 | 44508.125 |  | 51.38%
2021-11-08 04:00 | 44508.1667 |  | 51.74%
2021-11-08 05:00 | 44508.2083 |  | 52.41%
2021-11-08 06:00 | 44508.25 |  | 55.16%
2021-11-08 07:00 | 44508.2917 |  | 59.22%
2021-11-08 08:00 | 44508.3333 |  | 59.69%
2021-11-08 09:00 | 44508.375 |  | 59.32%
2021-11-08 10:00 | 44508.4167 |  | 58.93%
2021-11-08 11:00 | 44508.4583 |  | 58.87%
2021-11-08 12:00 | 44508.5 |  | 58.79%
2021-11-08 13:00 | 44508.5417 |  | 58.75%
2021-11-08 14:00 | 44508.5833 |  | 59.14%
2021-11-08 15:00 | 44508.625 |  | 59.35%
2021-11-08 16:00 | 44508.6667 |  | 59.73%
2021-11-08 17:00 | 44508.7083 |  | 60.11%
2021-11-08 18:00 | 44508.75 |  | 60.87%
2021-11-08 19:00 | 44508.7917 |  | 59.95%
2021-11-08 20:00 | 44508.8333 |  | 58.73%
2021-11-08 21:00 | 44508.875 |  | 57.47%
2021-11-08 22:00 | 44508.9167 |  | 56.22%
2021-11-08 23:00 | 44508.9583 |  | 55.43%
2021-11-09 | 44509 |  | 52.05%
2021-11-09 01:00 | 44509.0417 |  | 51.35%
2021-11-09 02:00 | 44509.0833 |  | 51.31%
2021-11-09 03:00 | 44509.125 |  | 51.61%
2021-11-09 04:00 | 44509.1667 |  | 51.97%
2021-11-09 05:00 | 44509.2083 |  | 52.64%
2021-11-09 06:00 | 44509.25 |  | 55.4%
2021-11-09 07:00 | 44509.2917 |  | 59.48%
2021-11-09 08:00 | 44509.3333 |  | 59.95%
2021-11-09 09:00 | 44509.375 |  | 59.58%
2021-11-09 10:00 | 44509.4167 |  | 59.19%
2021-11-09 11:00 | 44509.4583 |  | 59.13%
2021-11-09 12:00 | 44509.5 |  | 59.05%
2021-11-09 13:00 | 44509.5417 |  | 59.01%
2021-11-09 14:00 | 44509.5833 |  | 59.4%
2021-11-09 15:00 | 44509.625 |  | 59.61%
2021-11-09 16:00 | 44509.6667 |  | 60%
2021-11-09 17:00 | 44509.7083 |  | 60.38%
2021-11-09 18:00 | 44509.75 |  | 61.14%
2021-11-09 19:00 | 44509.7917 |  | 60.21%
2021-11-09 20:00 | 44509.8333 |  | 59%
2021-11-09 21:00 | 44509.875 |  | 57.72%
2021-11-09 22:00 | 44509.9167 |  | 56.47%
2021-11-09 23:00 | 44509.9583 |  | 55.68%
2021-11-10 | 44510 |  | 52.47%
2021-11-10 01:00 | 44510.0417 |  | 51.77%
2021-11-10 02:00 | 44510.0833 |  | 51.73%
2021-11-10 03:00 | 44510.125 |  | 52.03%
2021-11-10 04:00 | 44510.1667 |  | 52.39%
2021-11-10 05:00 | 44510.2083 |  | 53.07%
2021-11-10 06:00 | 44510.25 |  | 55.85%
2021-11-10 07:00 | 44510.2917 |  | 59.97%
2021-11-10 08:00 | 44510.3333 |  | 60.44%
2021-11-10 09:00 | 44510.375 |  | 60.06%
2021-11-10 10:00 | 44510.4167 |  | 59.67%
2021-11-10 11:00 | 44510.4583 |  | 59.61%
2021-11-10 12:00 | 44510.5 |  | 59.53%
2021-11-10 13:00 | 44510.5417 |  | 59.49%
2021-11-10 14:00 | 44510.5833 |  | 59.88%
2021-11-10 15:00 | 44510.625 |  | 60.1%
2021-11-10 16:00 | 44510.6667 |  | 60.48%
2021-11-10 17:00 | 44510.7083 |  | 60.87%
2021-11-10 18:00 | 44510.75 |  | 61.63%
2021-11-10 19:00 | 44510.7917 |  | 60.7%
2021-11-10 20:00 | 44510.8333 |  | 59.47%
2021-11-10 21:00 | 44510.875 |  | 58.19%
2021-11-10 22:00 | 44510.9167 |  | 56.93%
2021-11-10 23:00 | 44510.9583 |  | 56.13%
2021-11-11 | 44511 |  | 49.62%
2021-11-11 01:00 | 44511.0417 |  | 50.18%
2021-11-11 02:00 | 44511.0833 |  | 48.98%
2021-11-11 03:00 | 44511.125 |  | 48.53%
2021-11-11 04:00 | 44511.1667 |  | 48.28%
2021-11-11 05:00 | 44511.2083 |  | 48.81%
2021-11-11 06:00 | 44511.25 |  | 50.95%
2021-11-11 07:00 | 44511.2917 |  | 54.85%
2021-11-11 08:00 | 44511.3333 |  | 56.92%
2021-11-11 09:00 | 44511.375 |  | 57.79%
2021-11-11 10:00 | 44511.4167 |  | 57.71%
2021-11-11 11:00 | 44511.4583 |  | 57.45%
2021-11-11 12:00 | 44511.5 |  | 57.98%
2021-11-11 13:00 | 44511.5417 |  | 57.92%
2021-11-11 14:00 | 44511.5833 |  | 57.78%
2021-11-11 15:00 | 44511.625 |  | 57.66%
2021-11-11 16:00 | 44511.6667 |  | 57.5%
2021-11-11 17:00 | 44511.7083 |  | 57.51%
2021-11-11 18:00 | 44511.75 |  | 58.26%
2021-11-11 19:00 | 44511.7917 |  | 57.21%
2021-11-11 20:00 | 44511.8333 |  | 55.6%
2021-11-11 21:00 | 44511.875 |  | 53.96%
2021-11-11 22:00 | 44511.9167 |  | 52.21%
2021-11-11 23:00 | 44511.9583 |  | 51.57%
2021-11-12 | 44512 |  | 53.16%
2021-11-12 01:00 | 44512.0417 |  | 52.45%
2021-11-12 02:00 | 44512.0833 |  | 52.41%
2021-11-12 03:00 | 44512.125 |  | 52.72%
2021-11-12 04:00 | 44512.1667 |  | 53.08%
2021-11-12 05:00 | 44512.2083 |  | 53.77%
2021-11-12 06:00 | 44512.25 |  | 56.59%
2021-11-12 07:00 | 44512.2917 |  | 60.76%
2021-11-12 08:00 | 44512.3333 |  | 61.24%
2021-11-12 09:00 | 44512.375 |  | 60.86%
2021-11-12 10:00 | 44512.4167 |  | 60.46%
2021-11-12 11:00 | 44512.4583 |  | 60.4%
2021-11-12 12:00 | 44512.5 |  | 60.31%
2021-11-12 13:00 | 44512.5417 |  | 60.27%
2021-11-12 14:00 | 44512.5833 |  | 60.67%
2021-11-12 15:00 | 44512.625 |  | 60.89%
2021-11-12 16:00 | 44512.6667 |  | 61.28%
2021-11-12 17:00 | 44512.7083 |  | 61.67%
2021-11-12 18:00 | 44512.75 |  | 62.45%
2021-11-12 19:00 | 44512.7917 |  | 61.5%
2021-11-12 20:00 | 44512.8333 |  | 60.26%
2021-11-12 21:00 | 44512.875 |  | 58.96%
2021-11-12 22:00 | 44512.9167 |  | 57.68%
2021-11-12 23:00 | 44512.9583 |  | 56.87%
2021-11-13 | 44513 |  | 51.54%
2021-11-13 01:00 | 44513.0417 |  | 52.13%
2021-11-13 02:00 | 44513.0833 |  | 50.88%
2021-11-13 03:00 | 44513.125 |  | 50.41%
2021-11-13 04:00 | 44513.1667 |  | 50.15%
2021-11-13 05:00 | 44513.2083 |  | 50.71%
2021-11-13 06:00 | 44513.25 |  | 52.93%
2021-11-13 07:00 | 44513.2917 |  | 56.99%
2021-11-13 08:00 | 44513.3333 |  | 59.13%
2021-11-13 09:00 | 44513.375 |  | 60.04%
2021-11-13 10:00 | 44513.4167 |  | 59.96%
2021-11-13 11:00 | 44513.4583 |  | 59.69%
2021-11-13 12:00 | 44513.5 |  | 60.23%
2021-11-13 13:00 | 44513.5417 |  | 60.17%
2021-11-13 14:00 | 44513.5833 |  | 60.02%
2021-11-13 15:00 | 44513.625 |  | 59.9%
2021-11-13 16:00 | 44513.6667 |  | 59.73%
2021-11-13 17:00 | 44513.7083 |  | 59.75%
2021-11-13 18:00 | 44513.75 |  | 60.52%
2021-11-13 19:00 | 44513.7917 |  | 59.43%
2021-11-13 20:00 | 44513.8333 |  | 57.77%
2021-11-13 21:00 | 44513.875 |  | 56.06%
2021-11-13 22:00 | 44513.9167 |  | 54.24%
2021-11-13 23:00 | 44513.9583 |  | 53.58%
2021-11-14 | 44514 |  | 51.4%
2021-11-14 01:00 | 44514.0417 |  | 51.98%
2021-11-14 02:00 | 44514.0833 |  | 50.74%
2021-11-14 03:00 | 44514.125 |  | 50.27%
2021-11-14 04:00 | 44514.1667 |  | 50.01%
2021-11-14 05:00 | 44514.2083 |  | 50.57%
2021-11-14 06:00 | 44514.25 |  | 52.78%
2021-11-14 07:00 | 44514.2917 |  | 56.83%
2021-11-14 08:00 | 44514.3333 |  | 58.97%
2021-11-14 09:00 | 44514.375 |  | 59.87%
2021-11-14 10:00 | 44514.4167 |  | 59.79%
2021-11-14 11:00 | 44514.4583 |  | 59.52%
2021-11-14 12:00 | 44514.5 |  | 60.06%
2021-11-14 13:00 | 44514.5417 |  | 60.01%
2021-11-14 14:00 | 44514.5833 |  | 59.86%
2021-11-14 15:00 | 44514.625 |  | 59.74%
2021-11-14 16:00 | 44514.6667 |  | 59.56%
2021-11-14 17:00 | 44514.7083 |  | 59.58%
2021-11-14 18:00 | 44514.75 |  | 60.35%
2021-11-14 19:00 | 44514.7917 |  | 59.27%
2021-11-14 20:00 | 44514.8333 |  | 57.61%
2021-11-14 21:00 | 44514.875 |  | 55.9%
2021-11-14 22:00 | 44514.9167 |  | 54.09%
2021-11-14 23:00 | 44514.9583 |  | 53.43%
2021-11-15 | 44515 |  | 53.34%
2021-11-15 01:00 | 44515.0417 |  | 52.63%
2021-11-15 02:00 | 44515.0833 |  | 52.59%
2021-11-15 03:00 | 44515.125 |  | 52.89%
2021-11-15 04:00 | 44515.1667 |  | 53.26%
2021-11-15 05:00 | 44515.2083 |  | 53.95%
2021-11-15 06:00 | 44515.25 |  | 56.78%
2021-11-15 07:00 | 44515.2917 |  | 60.97%
2021-11-15 08:00 | 44515.3333 |  | 61.45%
2021-11-15 09:00 | 44515.375 |  | 61.06%
2021-11-15 10:00 | 44515.4167 |  | 60.67%
2021-11-15 11:00 | 44515.4583 |  | 60.6%
2021-11-15 12:00 | 44515.5 |  | 60.52%
2021-11-15 13:00 | 44515.5417 |  | 60.48%
2021-11-15 14:00 | 44515.5833 |  | 60.88%
2021-11-15 15:00 | 44515.625 |  | 61.1%
2021-11-15 16:00 | 44515.6667 |  | 61.49%
2021-11-15 17:00 | 44515.7083 |  | 61.88%
2021-11-15 18:00 | 44515.75 |  | 62.66%
2021-11-15 19:00 | 44515.7917 |  | 61.71%
2021-11-15 20:00 | 44515.8333 |  | 60.46%
2021-11-15 21:00 | 44515.875 |  | 59.16%
2021-11-15 22:00 | 44515.9167 |  | 57.88%
2021-11-15 23:00 | 44515.9583 |  | 57.07%
2021-11-16 | 44516 |  | 53.94%
2021-11-16 01:00 | 44516.0417 |  | 53.22%
2021-11-16 02:00 | 44516.0833 |  | 53.18%
2021-11-16 03:00 | 44516.125 |  | 53.49%
2021-11-16 04:00 | 44516.1667 |  | 53.86%
2021-11-16 05:00 | 44516.2083 |  | 54.55%
2021-11-16 06:00 | 44516.25 |  | 57.42%
2021-11-16 07:00 | 44516.2917 |  | 61.65%
2021-11-16 08:00 | 44516.3333 |  | 62.13%
2021-11-16 09:00 | 44516.375 |  | 61.75%
2021-11-16 10:00 | 44516.4167 |  | 61.35%
2021-11-16 11:00 | 44516.4583 |  | 61.28%
2021-11-16 12:00 | 44516.5 |  | 61.2%
2021-11-16 13:00 | 44516.5417 |  | 61.16%
2021-11-16 14:00 | 44516.5833 |  | 61.56%
2021-11-16 15:00 | 44516.625 |  | 61.78%
2021-11-16 16:00 | 44516.6667 |  | 62.18%
2021-11-16 17:00 | 44516.7083 |  | 62.58%
2021-11-16 18:00 | 44516.75 |  | 63.36%
2021-11-16 19:00 | 44516.7917 |  | 62.4%
2021-11-16 20:00 | 44516.8333 |  | 61.14%
2021-11-16 21:00 | 44516.875 |  | 59.82%
2021-11-16 22:00 | 44516.9167 |  | 58.53%
2021-11-16 23:00 | 44516.9583 |  | 57.7%
2021-11-17 | 44517 |  | 54.5%
2021-11-17 01:00 | 44517.0417 |  | 53.78%
2021-11-17 02:00 | 44517.0833 |  | 53.73%
2021-11-17 03:00 | 44517.125 |  | 54.05%
2021-11-17 04:00 | 44517.1667 |  | 54.42%
2021-11-17 05:00 | 44517.2083 |  | 55.13%
2021-11-17 06:00 | 44517.25 |  | 58.02%
2021-11-17 07:00 | 44517.2917 |  | 62.29%
2021-11-17 08:00 | 44517.3333 |  | 62.79%
2021-11-17 09:00 | 44517.375 |  | 62.39%
2021-11-17 10:00 | 44517.4167 |  | 61.99%
2021-11-17 11:00 | 44517.4583 |  | 61.92%
2021-11-17 12:00 | 44517.5 |  | 61.84%
2021-11-17 13:00 | 44517.5417 |  | 61.8%
2021-11-17 14:00 | 44517.5833 |  | 62.21%
2021-11-17 15:00 | 44517.625 |  | 62.43%
2021-11-17 16:00 | 44517.6667 |  | 62.83%
2021-11-17 17:00 | 44517.7083 |  | 63.23%
2021-11-17 18:00 | 44517.75 |  | 64.03%
2021-11-17 19:00 | 44517.7917 |  | 63.06%
2021-11-17 20:00 | 44517.8333 |  | 61.78%
2021-11-17 21:00 | 44517.875 |  | 60.45%
2021-11-17 22:00 | 44517.9167 |  | 59.14%
2021-11-17 23:00 | 44517.9583 |  | 58.31%
2021-11-18 | 44518 |  | 54.06%
2021-11-18 01:00 | 44518.0417 |  | 53.34%
2021-11-18 02:00 | 44518.0833 |  | 53.3%
2021-11-18 03:00 | 44518.125 |  | 53.61%
2021-11-18 04:00 | 44518.1667 |  | 53.98%
2021-11-18 05:00 | 44518.2083 |  | 54.68%
2021-11-18 06:00 | 44518.25 |  | 57.55%
2021-11-18 07:00 | 44518.2917 |  | 61.79%
2021-11-18 08:00 | 44518.3333 |  | 62.28%
2021-11-18 09:00 | 44518.375 |  | 61.89%
2021-11-18 10:00 | 44518.4167 |  | 61.48%
2021-11-18 11:00 | 44518.4583 |  | 61.42%
2021-11-18 12:00 | 44518.5 |  | 61.34%
2021-11-18 13:00 | 44518.5417 |  | 61.29%
2021-11-18 14:00 | 44518.5833 |  | 61.7%
2021-11-18 15:00 | 44518.625 |  | 61.92%
2021-11-18 16:00 | 44518.6667 |  | 62.32%
2021-11-18 17:00 | 44518.7083 |  | 62.72%
2021-11-18 18:00 | 44518.75 |  | 63.51%
2021-11-18 19:00 | 44518.7917 |  | 62.55%
2021-11-18 20:00 | 44518.8333 |  | 61.28%
2021-11-18 21:00 | 44518.875 |  | 59.96%
2021-11-18 22:00 | 44518.9167 |  | 58.66%
2021-11-18 23:00 | 44518.9583 |  | 57.84%
2021-11-19 | 44519 |  | 54%
2021-11-19 01:00 | 44519.0417 |  | 53.28%
2021-11-19 02:00 | 44519.0833 |  | 53.24%
2021-11-19 03:00 | 44519.125 |  | 53.55%
2021-11-19 04:00 | 44519.1667 |  | 53.92%
2021-11-19 05:00 | 44519.2083 |  | 54.62%
2021-11-19 06:00 | 44519.25 |  | 57.49%
2021-11-19 07:00 | 44519.2917 |  | 61.72%
2021-11-19 08:00 | 44519.3333 |  | 62.21%
2021-11-19 09:00 | 44519.375 |  | 61.82%
2021-11-19 10:00 | 44519.4167 |  | 61.42%
2021-11-19 11:00 | 44519.4583 |  | 61.35%
2021-11-19 12:00 | 44519.5 |  | 61.27%
2021-11-19 13:00 | 44519.5417 |  | 61.23%
2021-11-19 14:00 | 44519.5833 |  | 61.63%
2021-11-19 15:00 | 44519.625 |  | 61.85%
2021-11-19 16:00 | 44519.6667 |  | 62.25%
2021-11-19 17:00 | 44519.7083 |  | 62.65%
2021-11-19 18:00 | 44519.75 |  | 63.44%
2021-11-19 19:00 | 44519.7917 |  | 62.48%
2021-11-19 20:00 | 44519.8333 |  | 61.21%
2021-11-19 21:00 | 44519.875 |  | 59.89%
2021-11-19 22:00 | 44519.9167 |  | 58.59%
2021-11-19 23:00 | 44519.9583 |  | 57.77%
2021-11-20 | 44520 |  | 52.26%
2021-11-20 01:00 | 44520.0417 |  | 52.85%
2021-11-20 02:00 | 44520.0833 |  | 51.59%
2021-11-20 03:00 | 44520.125 |  | 51.11%
2021-11-20 04:00 | 44520.1667 |  | 50.85%
2021-11-20 05:00 | 44520.2083 |  | 51.41%
2021-11-20 06:00 | 44520.25 |  | 53.67%
2021-11-20 07:00 | 44520.2917 |  | 57.78%
2021-11-20 08:00 | 44520.3333 |  | 59.96%
2021-11-20 09:00 | 44520.375 |  | 60.87%
2021-11-20 10:00 | 44520.4167 |  | 60.79%
2021-11-20 11:00 | 44520.4583 |  | 60.51%
2021-11-20 12:00 | 44520.5 |  | 61.07%
2021-11-20 13:00 | 44520.5417 |  | 61.01%
2021-11-20 14:00 | 44520.5833 |  | 60.86%
2021-11-20 15:00 | 44520.625 |  | 60.74%
2021-11-20 16:00 | 44520.6667 |  | 60.56%
2021-11-20 17:00 | 44520.7083 |  | 60.58%
2021-11-20 18:00 | 44520.75 |  | 61.36%
2021-11-20 19:00 | 44520.7917 |  | 60.26%
2021-11-20 20:00 | 44520.8333 |  | 58.57%
2021-11-20 21:00 | 44520.875 |  | 56.84%
2021-11-20 22:00 | 44520.9167 |  | 54.99%
2021-11-20 23:00 | 44520.9583 |  | 54.32%
2021-11-21 | 44521 |  | 51.75%
2021-11-21 01:00 | 44521.0417 |  | 52.34%
2021-11-21 02:00 | 44521.0833 |  | 51.08%
2021-11-21 03:00 | 44521.125 |  | 50.61%
2021-11-21 04:00 | 44521.1667 |  | 50.35%
2021-11-21 05:00 | 44521.2083 |  | 50.91%
2021-11-21 06:00 | 44521.25 |  | 53.14%
2021-11-21 07:00 | 44521.2917 |  | 57.21%
2021-11-21 08:00 | 44521.3333 |  | 59.37%
2021-11-21 09:00 | 44521.375 |  | 60.27%
2021-11-21 10:00 | 44521.4167 |  | 60.19%
2021-11-21 11:00 | 44521.4583 |  | 59.92%
2021-11-21 12:00 | 44521.5 |  | 60.47%
2021-11-21 13:00 | 44521.5417 |  | 60.41%
2021-11-21 14:00 | 44521.5833 |  | 60.26%
2021-11-21 15:00 | 44521.625 |  | 60.14%
2021-11-21 16:00 | 44521.6667 |  | 59.97%
2021-11-21 17:00 | 44521.7083 |  | 59.98%
2021-11-21 18:00 | 44521.75 |  | 60.76%
2021-11-21 19:00 | 44521.7917 |  | 59.67%
2021-11-21 20:00 | 44521.8333 |  | 57.99%
2021-11-21 21:00 | 44521.875 |  | 56.28%
2021-11-21 22:00 | 44521.9167 |  | 54.45%
2021-11-21 23:00 | 44521.9583 |  | 53.79%
2021-11-22 | 44522 |  | 53.76%
2021-11-22 01:00 | 44522.0417 |  | 53.04%
2021-11-22 02:00 | 44522.0833 |  | 53%
2021-11-22 03:00 | 44522.125 |  | 53.31%
2021-11-22 04:00 | 44522.1667 |  | 53.68%
2021-11-22 05:00 | 44522.2083 |  | 54.37%
2021-11-22 06:00 | 44522.25 |  | 57.23%
2021-11-22 07:00 | 44522.2917 |  | 61.44%
2021-11-22 08:00 | 44522.3333 |  | 61.93%
2021-11-22 09:00 | 44522.375 |  | 61.54%
2021-11-22 10:00 | 44522.4167 |  | 61.14%
2021-11-22 11:00 | 44522.4583 |  | 61.07%
2021-11-22 12:00 | 44522.5 |  | 60.99%
2021-11-22 13:00 | 44522.5417 |  | 60.95%
2021-11-22 14:00 | 44522.5833 |  | 61.35%
2021-11-22 15:00 | 44522.625 |  | 61.58%
2021-11-22 16:00 | 44522.6667 |  | 61.97%
2021-11-22 17:00 | 44522.7083 |  | 62.37%
2021-11-22 18:00 | 44522.75 |  | 63.15%
2021-11-22 19:00 | 44522.7917 |  | 62.19%
2021-11-22 20:00 | 44522.8333 |  | 60.94%
2021-11-22 21:00 | 44522.875 |  | 59.62%
2021-11-22 22:00 | 44522.9167 |  | 58.33%
2021-11-22 23:00 | 44522.9583 |  | 57.51%
2021-11-23 | 44523 |  | 54.16%
2021-11-23 01:00 | 44523.0417 |  | 53.43%
2021-11-23 02:00 | 44523.0833 |  | 53.39%
2021-11-23 03:00 | 44523.125 |  | 53.7%
2021-11-23 04:00 | 44523.1667 |  | 54.08%
2021-11-23 05:00 | 44523.2083 |  | 54.77%
2021-11-23 06:00 | 44523.25 |  | 57.65%
2021-11-23 07:00 | 44523.2917 |  | 61.9%
2021-11-23 08:00 | 44523.3333 |  | 62.39%
2021-11-23 09:00 | 44523.375 |  | 62%
2021-11-23 10:00 | 44523.4167 |  | 61.59%
2021-11-23 11:00 | 44523.4583 |  | 61.53%
2021-11-23 12:00 | 44523.5 |  | 61.44%
2021-11-23 13:00 | 44523.5417 |  | 61.4%
2021-11-23 14:00 | 44523.5833 |  | 61.81%
2021-11-23 15:00 | 44523.625 |  | 62.03%
2021-11-23 16:00 | 44523.6667 |  | 62.43%
2021-11-23 17:00 | 44523.7083 |  | 62.83%
2021-11-23 18:00 | 44523.75 |  | 63.62%
2021-11-23 19:00 | 44523.7917 |  | 62.66%
2021-11-23 20:00 | 44523.8333 |  | 61.39%
2021-11-23 21:00 | 44523.875 |  | 60.06%
2021-11-23 22:00 | 44523.9167 |  | 58.76%
2021-11-23 23:00 | 44523.9583 |  | 57.94%
2021-11-24 | 44524 |  | 54.41%
2021-11-24 01:00 | 44524.0417 |  | 53.68%
2021-11-24 02:00 | 44524.0833 |  | 53.64%
2021-11-24 03:00 | 44524.125 |  | 53.95%
2021-11-24 04:00 | 44524.1667 |  | 54.32%
2021-11-24 05:00 | 44524.2083 |  | 55.03%
2021-11-24 06:00 | 44524.25 |  | 57.92%
2021-11-24 07:00 | 44524.2917 |  | 62.18%
2021-11-24 08:00 | 44524.3333 |  | 62.67%
2021-11-24 09:00 | 44524.375 |  | 62.28%
2021-11-24 10:00 | 44524.4167 |  | 61.88%
2021-11-24 11:00 | 44524.4583 |  | 61.81%
2021-11-24 12:00 | 44524.5 |  | 61.72%
2021-11-24 13:00 | 44524.5417 |  | 61.68%
2021-11-24 14:00 | 44524.5833 |  | 62.09%
2021-11-24 15:00 | 44524.625 |  | 62.32%
2021-11-24 16:00 | 44524.6667 |  | 62.72%
2021-11-24 17:00 | 44524.7083 |  | 63.12%
2021-11-24 18:00 | 44524.75 |  | 63.91%
2021-11-24 19:00 | 44524.7917 |  | 62.94%
2021-11-24 20:00 | 44524.8333 |  | 61.67%
2021-11-24 21:00 | 44524.875 |  | 60.34%
2021-11-24 22:00 | 44524.9167 |  | 59.03%
2021-11-24 23:00 | 44524.9583 |  | 58.2%
2021-11-25 | 44525 |  | 54.51%
2021-11-25 01:00 | 44525.0417 |  | 53.78%
2021-11-25 02:00 | 44525.0833 |  | 53.74%
2021-11-25 03:00 | 44525.125 |  | 54.05%
2021-11-25 04:00 | 44525.1667 |  | 54.43%
2021-11-25 05:00 | 44525.2083 |  | 55.13%
2021-11-25 06:00 | 44525.25 |  | 58.03%
2021-11-25 07:00 | 44525.2917 |  | 62.3%
2021-11-25 08:00 | 44525.3333 |  | 62.79%
2021-11-25 09:00 | 44525.375 |  | 62.4%
2021-11-25 10:00 | 44525.4167 |  | 61.99%
2021-11-25 11:00 | 44525.4583 |  | 61.93%
2021-11-25 12:00 | 44525.5 |  | 61.84%
2021-11-25 13:00 | 44525.5417 |  | 61.8%
2021-11-25 14:00 | 44525.5833 |  | 62.21%
2021-11-25 15:00 | 44525.625 |  | 62.44%
2021-11-25 16:00 | 44525.6667 |  | 62.84%
2021-11-25 17:00 | 44525.7083 |  | 63.24%
2021-11-25 18:00 | 44525.75 |  | 64.03%
2021-11-25 19:00 | 44525.7917 |  | 63.06%
2021-11-25 20:00 | 44525.8333 |  | 61.79%
2021-11-25 21:00 | 44525.875 |  | 60.45%
2021-11-25 22:00 | 44525.9167 |  | 59.14%
2021-11-25 23:00 | 44525.9583 |  | 58.31%
2021-11-26 | 44526 |  | 54.66%
2021-11-26 01:00 | 44526.0417 |  | 53.93%
2021-11-26 02:00 | 44526.0833 |  | 53.89%
2021-11-26 03:00 | 44526.125 |  | 54.2%
2021-11-26 04:00 | 44526.1667 |  | 54.57%
2021-11-26 05:00 | 44526.2083 |  | 55.28%
2021-11-26 06:00 | 44526.25 |  | 58.18%
2021-11-26 07:00 | 44526.2917 |  | 62.47%
2021-11-26 08:00 | 44526.3333 |  | 62.96%
2021-11-26 09:00 | 44526.375 |  | 62.57%
2021-11-26 10:00 | 44526.4167 |  | 62.16%
2021-11-26 11:00 | 44526.4583 |  | 62.1%
2021-11-26 12:00 | 44526.5 |  | 62.01%
2021-11-26 13:00 | 44526.5417 |  | 61.97%
2021-11-26 14:00 | 44526.5833 |  | 62.38%
2021-11-26 15:00 | 44526.625 |  | 62.61%
2021-11-26 16:00 | 44526.6667 |  | 63.01%
2021-11-26 17:00 | 44526.7083 |  | 63.41%
2021-11-26 18:00 | 44526.75 |  | 64.21%
2021-11-26 19:00 | 44526.7917 |  | 63.24%
2021-11-26 20:00 | 44526.8333 |  | 61.96%
2021-11-26 21:00 | 44526.875 |  | 60.62%
2021-11-26 22:00 | 44526.9167 |  | 59.31%
2021-11-26 23:00 | 44526.9583 |  | 58.47%
2021-11-27 | 44527 |  | 53.4%
2021-11-27 01:00 | 44527.0417 |  | 54.19%
2021-11-27 02:00 | 44527.0833 |  | 53.79%
2021-11-27 03:00 | 44527.125 |  | 53.11%
2021-11-27 04:00 | 44527.1667 |  | 51.97%
2021-11-27 05:00 | 44527.2083 |  | 51.64%
2021-11-27 06:00 | 44527.25 |  | 52.53%
2021-11-27 07:00 | 44527.2917 |  | 53.46%
2021-11-27 08:00 | 44527.3333 |  | 55.26%
2021-11-27 09:00 | 44527.375 |  | 56.99%
2021-11-27 10:00 | 44527.4167 |  | 58.17%
2021-11-27 11:00 | 44527.4583 |  | 58.4%
2021-11-27 12:00 | 44527.5 |  | 58.97%
2021-11-27 13:00 | 44527.5417 |  | 58.79%
2021-11-27 14:00 | 44527.5833 |  | 59.17%
2021-11-27 15:00 | 44527.625 |  | 59%
2021-11-27 16:00 | 44527.6667 |  | 58.86%
2021-11-27 17:00 | 44527.7083 |  | 58.16%
2021-11-27 18:00 | 44527.75 |  | 55.24%
2021-11-27 19:00 | 44527.7917 |  | 53.63%
2021-11-27 20:00 | 44527.8333 |  | 52.35%
2021-11-27 21:00 | 44527.875 |  | 51%
2021-11-27 22:00 | 44527.9167 |  | 50.78%
2021-11-27 23:00 | 44527.9583 |  | 52.63%
2021-11-28 | 44528 |  | 53.28%
2021-11-28 01:00 | 44528.0417 |  | 54.08%
2021-11-28 02:00 | 44528.0833 |  | 53.68%
2021-11-28 03:00 | 44528.125 |  | 53%
2021-11-28 04:00 | 44528.1667 |  | 51.86%
2021-11-28 05:00 | 44528.2083 |  | 51.54%
2021-11-28 06:00 | 44528.25 |  | 52.41%
2021-11-28 07:00 | 44528.2917 |  | 53.34%
2021-11-28 08:00 | 44528.3333 |  | 55.14%
2021-11-28 09:00 | 44528.375 |  | 56.87%
2021-11-28 10:00 | 44528.4167 |  | 58.05%
2021-11-28 11:00 | 44528.4583 |  | 58.27%
2021-11-28 12:00 | 44528.5 |  | 58.84%
2021-11-28 13:00 | 44528.5417 |  | 58.66%
2021-11-28 14:00 | 44528.5833 |  | 59.04%
2021-11-28 15:00 | 44528.625 |  | 58.88%
2021-11-28 16:00 | 44528.6667 |  | 58.73%
2021-11-28 17:00 | 44528.7083 |  | 58.04%
2021-11-28 18:00 | 44528.75 |  | 55.12%
2021-11-28 19:00 | 44528.7917 |  | 53.51%
2021-11-28 20:00 | 44528.8333 |  | 52.24%
2021-11-28 21:00 | 44528.875 |  | 50.89%
2021-11-28 22:00 | 44528.9167 |  | 50.68%
2021-11-28 23:00 | 44528.9583 |  | 52.52%
2021-11-29 | 44529 |  | 54.56%
2021-11-29 01:00 | 44529.0417 |  | 54.34%
2021-11-29 02:00 | 44529.0833 |  | 54.16%
2021-11-29 03:00 | 44529.125 |  | 54.03%
2021-11-29 04:00 | 44529.1667 |  | 53.39%
2021-11-29 05:00 | 44529.2083 |  | 53.65%
2021-11-29 06:00 | 44529.25 |  | 55.16%
2021-11-29 07:00 | 44529.2917 |  | 57.85%
2021-11-29 08:00 | 44529.3333 |  | 59.25%
2021-11-29 09:00 | 44529.375 |  | 59.3%
2021-11-29 10:00 | 44529.4167 |  | 59.51%
2021-11-29 11:00 | 44529.4583 |  | 59.51%
2021-11-29 12:00 | 44529.5 |  | 59.79%
2021-11-29 13:00 | 44529.5417 |  | 59.92%
2021-11-29 14:00 | 44529.5833 |  | 60%
2021-11-29 15:00 | 44529.625 |  | 60.2%
2021-11-29 16:00 | 44529.6667 |  | 60.44%
2021-11-29 17:00 | 44529.7083 |  | 60.25%
2021-11-29 18:00 | 44529.75 |  | 60.18%
2021-11-29 19:00 | 44529.7917 |  | 59.1%
2021-11-29 20:00 | 44529.8333 |  | 57.87%
2021-11-29 21:00 | 44529.875 |  | 55.91%
2021-11-29 22:00 | 44529.9167 |  | 54.49%
2021-11-29 23:00 | 44529.9583 |  | 54.91%
2021-11-30 | 44530 |  | 54.43%
2021-11-30 01:00 | 44530.0417 |  | 54.21%
2021-11-30 02:00 | 44530.0833 |  | 54.03%
2021-11-30 03:00 | 44530.125 |  | 53.9%
2021-11-30 04:00 | 44530.1667 |  | 53.27%
2021-11-30 05:00 | 44530.2083 |  | 53.53%
2021-11-30 06:00 | 44530.25 |  | 55.03%
2021-11-30 07:00 | 44530.2917 |  | 57.72%
2021-11-30 08:00 | 44530.3333 |  | 59.11%
2021-11-30 09:00 | 44530.375 |  | 59.15%
2021-11-30 10:00 | 44530.4167 |  | 59.37%
2021-11-30 11:00 | 44530.4583 |  | 59.36%
2021-11-30 12:00 | 44530.5 |  | 59.65%
2021-11-30 13:00 | 44530.5417 |  | 59.77%
2021-11-30 14:00 | 44530.5833 |  | 59.86%
2021-11-30 15:00 | 44530.625 |  | 60.06%
2021-11-30 16:00 | 44530.6667 |  | 60.3%
2021-11-30 17:00 | 44530.7083 |  | 60.1%
2021-11-30 18:00 | 44530.75 |  | 60.04%
2021-11-30 19:00 | 44530.7917 |  | 58.96%
2021-11-30 20:00 | 44530.8333 |  | 57.73%
2021-11-30 21:00 | 44530.875 |  | 55.77%
2021-11-30 22:00 | 44530.9167 |  | 54.36%
2021-11-30 23:00 | 44530.9583 |  | 54.78%
2021-12-01 | 44531 |  | 54.07%
2021-12-01 01:00 | 44531.0417 |  | 53.86%
2021-12-01 02:00 | 44531.0833 |  | 53.68%
2021-12-01 03:00 | 44531.125 |  | 53.55%
2021-12-01 04:00 | 44531.1667 |  | 52.92%
2021-12-01 05:00 | 44531.2083 |  | 53.18%
2021-12-01 06:00 | 44531.25 |  | 54.68%
2021-12-01 07:00 | 44531.2917 |  | 57.34%
2021-12-01 08:00 | 44531.3333 |  | 58.73%
2021-12-01 09:00 | 44531.375 |  | 58.77%
2021-12-01 10:00 | 44531.4167 |  | 58.98%
2021-12-01 11:00 | 44531.4583 |  | 58.98%
2021-12-01 12:00 | 44531.5 |  | 59.26%
2021-12-01 13:00 | 44531.5417 |  | 59.38%
2021-12-01 14:00 | 44531.5833 |  | 59.47%
2021-12-01 15:00 | 44531.625 |  | 59.67%
2021-12-01 16:00 | 44531.6667 |  | 59.9%
2021-12-01 17:00 | 44531.7083 |  | 59.71%
2021-12-01 18:00 | 44531.75 |  | 59.65%
2021-12-01 19:00 | 44531.7917 |  | 58.57%
2021-12-01 20:00 | 44531.8333 |  | 57.36%
2021-12-01 21:00 | 44531.875 |  | 55.41%
2021-12-01 22:00 | 44531.9167 |  | 54.01%
2021-12-01 23:00 | 44531.9583 |  | 54.42%
2021-12-02 | 44532 |  | 54.56%
2021-12-02 01:00 | 44532.0417 |  | 54.35%
2021-12-02 02:00 | 44532.0833 |  | 54.16%
2021-12-02 03:00 | 44532.125 |  | 54.04%
2021-12-02 04:00 | 44532.1667 |  | 53.4%
2021-12-02 05:00 | 44532.2083 |  | 53.66%
2021-12-02 06:00 | 44532.25 |  | 55.17%
2021-12-02 07:00 | 44532.2917 |  | 57.86%
2021-12-02 08:00 | 44532.3333 |  | 59.26%
2021-12-02 09:00 | 44532.375 |  | 59.3%
2021-12-02 10:00 | 44532.4167 |  | 59.51%
2021-12-02 11:00 | 44532.4583 |  | 59.51%
2021-12-02 12:00 | 44532.5 |  | 59.8%
2021-12-02 13:00 | 44532.5417 |  | 59.92%
2021-12-02 14:00 | 44532.5833 |  | 60%
2021-12-02 15:00 | 44532.625 |  | 60.2%
2021-12-02 16:00 | 44532.6667 |  | 60.44%
2021-12-02 17:00 | 44532.7083 |  | 60.25%
2021-12-02 18:00 | 44532.75 |  | 60.19%
2021-12-02 19:00 | 44532.7917 |  | 59.1%
2021-12-02 20:00 | 44532.8333 |  | 57.87%
2021-12-02 21:00 | 44532.875 |  | 55.91%
2021-12-02 22:00 | 44532.9167 |  | 54.5%
2021-12-02 23:00 | 44532.9583 |  | 54.92%
2021-12-03 | 44533 |  | 54.96%
2021-12-03 01:00 | 44533.0417 |  | 54.75%
2021-12-03 02:00 | 44533.0833 |  | 54.56%
2021-12-03 03:00 | 44533.125 |  | 54.44%
2021-12-03 04:00 | 44533.1667 |  | 53.79%
2021-12-03 05:00 | 44533.2083 |  | 54.05%
2021-12-03 06:00 | 44533.25 |  | 55.58%
2021-12-03 07:00 | 44533.2917 |  | 58.28%
2021-12-03 08:00 | 44533.3333 |  | 59.7%
2021-12-03 09:00 | 44533.375 |  | 59.74%
2021-12-03 10:00 | 44533.4167 |  | 59.95%
2021-12-03 11:00 | 44533.4583 |  | 59.95%
2021-12-03 12:00 | 44533.5 |  | 60.24%
2021-12-03 13:00 | 44533.5417 |  | 60.36%
2021-12-03 14:00 | 44533.5833 |  | 60.45%
2021-12-03 15:00 | 44533.625 |  | 60.65%
2021-12-03 16:00 | 44533.6667 |  | 60.89%
2021-12-03 17:00 | 44533.7083 |  | 60.7%
2021-12-03 18:00 | 44533.75 |  | 60.63%
2021-12-03 19:00 | 44533.7917 |  | 59.54%
2021-12-03 20:00 | 44533.8333 |  | 58.3%
2021-12-03 21:00 | 44533.875 |  | 56.32%
2021-12-03 22:00 | 44533.9167 |  | 54.9%
2021-12-03 23:00 | 44533.9583 |  | 55.32%
2021-12-04 | 44534 |  | 53.96%
2021-12-04 01:00 | 44534.0417 |  | 54.76%
2021-12-04 02:00 | 44534.0833 |  | 54.36%
2021-12-04 03:00 | 44534.125 |  | 53.67%
2021-12-04 04:00 | 44534.1667 |  | 52.52%
2021-12-04 05:00 | 44534.2083 |  | 52.19%
2021-12-04 06:00 | 44534.25 |  | 53.08%
2021-12-04 07:00 | 44534.2917 |  | 54.02%
2021-12-04 08:00 | 44534.3333 |  | 55.84%
2021-12-04 09:00 | 44534.375 |  | 57.59%
2021-12-04 10:00 | 44534.4167 |  | 58.78%
2021-12-04 11:00 | 44534.4583 |  | 59.01%
2021-12-04 12:00 | 44534.5 |  | 59.59%
2021-12-04 13:00 | 44534.5417 |  | 59.41%
2021-12-04 14:00 | 44534.5833 |  | 59.79%
2021-12-04 15:00 | 44534.625 |  | 59.63%
2021-12-04 16:00 | 44534.6667 |  | 59.48%
2021-12-04 17:00 | 44534.7083 |  | 58.78%
2021-12-04 18:00 | 44534.75 |  | 55.82%
2021-12-04 19:00 | 44534.7917 |  | 54.19%
2021-12-04 20:00 | 44534.8333 |  | 52.9%
2021-12-04 21:00 | 44534.875 |  | 51.54%
2021-12-04 22:00 | 44534.9167 |  | 51.32%
2021-12-04 23:00 | 44534.9583 |  | 53.19%
2021-12-05 | 44535 |  | 54.07%
2021-12-05 01:00 | 44535.0417 |  | 54.87%
2021-12-05 02:00 | 44535.0833 |  | 54.47%
2021-12-05 03:00 | 44535.125 |  | 53.78%
2021-12-05 04:00 | 44535.1667 |  | 52.62%
2021-12-05 05:00 | 44535.2083 |  | 52.29%
2021-12-05 06:00 | 44535.25 |  | 53.19%
2021-12-05 07:00 | 44535.2917 |  | 54.13%
2021-12-05 08:00 | 44535.3333 |  | 55.96%
2021-12-05 09:00 | 44535.375 |  | 57.71%
2021-12-05 10:00 | 44535.4167 |  | 58.9%
2021-12-05 11:00 | 44535.4583 |  | 59.13%
2021-12-05 12:00 | 44535.5 |  | 59.71%
2021-12-05 13:00 | 44535.5417 |  | 59.53%
2021-12-05 14:00 | 44535.5833 |  | 59.91%
2021-12-05 15:00 | 44535.625 |  | 59.75%
2021-12-05 16:00 | 44535.6667 |  | 59.6%
2021-12-05 17:00 | 44535.7083 |  | 58.89%
2021-12-05 18:00 | 44535.75 |  | 55.93%
2021-12-05 19:00 | 44535.7917 |  | 54.3%
2021-12-05 20:00 | 44535.8333 |  | 53%
2021-12-05 21:00 | 44535.875 |  | 51.64%
2021-12-05 22:00 | 44535.9167 |  | 51.42%
2021-12-05 23:00 | 44535.9583 |  | 53.29%
2021-12-06 | 44536 |  | 55.77%
2021-12-06 01:00 | 44536.0417 |  | 55.56%
2021-12-06 02:00 | 44536.0833 |  | 55.37%
2021-12-06 03:00 | 44536.125 |  | 55.24%
2021-12-06 04:00 | 44536.1667 |  | 54.59%
2021-12-06 05:00 | 44536.2083 |  | 54.85%
2021-12-06 06:00 | 44536.25 |  | 56.4%
2021-12-06 07:00 | 44536.2917 |  | 59.15%
2021-12-06 08:00 | 44536.3333 |  | 60.58%
2021-12-06 09:00 | 44536.375 |  | 60.62%
2021-12-06 10:00 | 44536.4167 |  | 60.84%
2021-12-06 11:00 | 44536.4583 |  | 60.84%
2021-12-06 12:00 | 44536.5 |  | 61.13%
2021-12-06 13:00 | 44536.5417 |  | 61.25%
2021-12-06 14:00 | 44536.5833 |  | 61.34%
2021-12-06 15:00 | 44536.625 |  | 61.55%
2021-12-06 16:00 | 44536.6667 |  | 61.79%
2021-12-06 17:00 | 44536.7083 |  | 61.59%
2021-12-06 18:00 | 44536.75 |  | 61.53%
2021-12-06 19:00 | 44536.7917 |  | 60.42%
2021-12-06 20:00 | 44536.8333 |  | 59.16%
2021-12-06 21:00 | 44536.875 |  | 57.16%
2021-12-06 22:00 | 44536.9167 |  | 55.71%
2021-12-06 23:00 | 44536.9583 |  | 56.14%
2021-12-07 | 44537 |  | 55.38%
2021-12-07 01:00 | 44537.0417 |  | 55.17%
2021-12-07 02:00 | 44537.0833 |  | 54.98%
2021-12-07 03:00 | 44537.125 |  | 54.85%
2021-12-07 04:00 | 44537.1667 |  | 54.2%
2021-12-07 05:00 | 44537.2083 |  | 54.47%
2021-12-07 06:00 | 44537.25 |  | 56%
2021-12-07 07:00 | 44537.2917 |  | 58.73%
2021-12-07 08:00 | 44537.3333 |  | 60.15%
2021-12-07 09:00 | 44537.375 |  | 60.19%
2021-12-07 10:00 | 44537.4167 |  | 60.41%
2021-12-07 11:00 | 44537.4583 |  | 60.41%
2021-12-07 12:00 | 44537.5 |  | 60.7%
2021-12-07 13:00 | 44537.5417 |  | 60.82%
2021-12-07 14:00 | 44537.5833 |  | 60.91%
2021-12-07 15:00 | 44537.625 |  | 61.11%
2021-12-07 16:00 | 44537.6667 |  | 61.36%
2021-12-07 17:00 | 44537.7083 |  | 61.16%
2021-12-07 18:00 | 44537.75 |  | 61.09%
2021-12-07 19:00 | 44537.7917 |  | 59.99%
2021-12-07 20:00 | 44537.8333 |  | 58.75%
2021-12-07 21:00 | 44537.875 |  | 56.76%
2021-12-07 22:00 | 44537.9167 |  | 55.32%
2021-12-07 23:00 | 44537.9583 |  | 55.74%
2021-12-08 | 44538 |  | 55.12%
2021-12-08 01:00 | 44538.0417 |  | 54.9%
2021-12-08 02:00 | 44538.0833 |  | 54.72%
2021-12-08 03:00 | 44538.125 |  | 54.59%
2021-12-08 04:00 | 44538.1667 |  | 53.94%
2021-12-08 05:00 | 44538.2083 |  | 54.2%
2021-12-08 06:00 | 44538.25 |  | 55.73%
2021-12-08 07:00 | 44538.2917 |  | 58.45%
2021-12-08 08:00 | 44538.3333 |  | 59.86%
2021-12-08 09:00 | 44538.375 |  | 59.9%
2021-12-08 10:00 | 44538.4167 |  | 60.12%
2021-12-08 11:00 | 44538.4583 |  | 60.12%
2021-12-08 12:00 | 44538.5 |  | 60.41%
2021-12-08 13:00 | 44538.5417 |  | 60.53%
2021-12-08 14:00 | 44538.5833 |  | 60.62%
2021-12-08 15:00 | 44538.625 |  | 60.82%
2021-12-08 16:00 | 44538.6667 |  | 61.06%
2021-12-08 17:00 | 44538.7083 |  | 60.87%
2021-12-08 18:00 | 44538.75 |  | 60.8%
2021-12-08 19:00 | 44538.7917 |  | 59.7%
2021-12-08 20:00 | 44538.8333 |  | 58.46%
2021-12-08 21:00 | 44538.875 |  | 56.48%
2021-12-08 22:00 | 44538.9167 |  | 55.05%
2021-12-08 23:00 | 44538.9583 |  | 55.48%
2021-12-09 | 44539 |  | 55.29%
2021-12-09 01:00 | 44539.0417 |  | 55.08%
2021-12-09 02:00 | 44539.0833 |  | 54.89%
2021-12-09 03:00 | 44539.125 |  | 54.76%
2021-12-09 04:00 | 44539.1667 |  | 54.11%
2021-12-09 05:00 | 44539.2083 |  | 54.38%
2021-12-09 06:00 | 44539.25 |  | 55.91%
2021-12-09 07:00 | 44539.2917 |  | 58.63%
2021-12-09 08:00 | 44539.3333 |  | 60.05%
2021-12-09 09:00 | 44539.375 |  | 60.1%
2021-12-09 10:00 | 44539.4167 |  | 60.31%
2021-12-09 11:00 | 44539.4583 |  | 60.31%
2021-12-09 12:00 | 44539.5 |  | 60.6%
2021-12-09 13:00 | 44539.5417 |  | 60.72%
2021-12-09 14:00 | 44539.5833 |  | 60.81%
2021-12-09 15:00 | 44539.625 |  | 61.01%
2021-12-09 16:00 | 44539.6667 |  | 61.26%
2021-12-09 17:00 | 44539.7083 |  | 61.06%
2021-12-09 18:00 | 44539.75 |  | 60.99%
2021-12-09 19:00 | 44539.7917 |  | 59.89%
2021-12-09 20:00 | 44539.8333 |  | 58.65%
2021-12-09 21:00 | 44539.875 |  | 56.66%
2021-12-09 22:00 | 44539.9167 |  | 55.23%
2021-12-09 23:00 | 44539.9583 |  | 55.65%
2021-12-10 | 44540 |  | 55.65%
2021-12-10 01:00 | 44540.0417 |  | 55.43%
2021-12-10 02:00 | 44540.0833 |  | 55.25%
2021-12-10 03:00 | 44540.125 |  | 55.12%
2021-12-10 04:00 | 44540.1667 |  | 54.47%
2021-12-10 05:00 | 44540.2083 |  | 54.73%
2021-12-10 06:00 | 44540.25 |  | 56.27%
2021-12-10 07:00 | 44540.2917 |  | 59.02%
2021-12-10 08:00 | 44540.3333 |  | 60.44%
2021-12-10 09:00 | 44540.375 |  | 60.49%
2021-12-10 10:00 | 44540.4167 |  | 60.7%
2021-12-10 11:00 | 44540.4583 |  | 60.7%
2021-12-10 12:00 | 44540.5 |  | 61%
2021-12-10 13:00 | 44540.5417 |  | 61.12%
2021-12-10 14:00 | 44540.5833 |  | 61.21%
2021-12-10 15:00 | 44540.625 |  | 61.41%
2021-12-10 16:00 | 44540.6667 |  | 61.65%
2021-12-10 17:00 | 44540.7083 |  | 61.46%
2021-12-10 18:00 | 44540.75 |  | 61.39%
2021-12-10 19:00 | 44540.7917 |  | 60.28%
2021-12-10 20:00 | 44540.8333 |  | 59.03%
2021-12-10 21:00 | 44540.875 |  | 57.03%
2021-12-10 22:00 | 44540.9167 |  | 55.59%
2021-12-10 23:00 | 44540.9583 |  | 56.01%
2021-12-11 | 44541 |  | 54.29%
2021-12-11 01:00 | 44541.0417 |  | 55.1%
2021-12-11 02:00 | 44541.0833 |  | 54.69%
2021-12-11 03:00 | 44541.125 |  | 54%
2021-12-11 04:00 | 44541.1667 |  | 52.84%
2021-12-11 05:00 | 44541.2083 |  | 52.51%
2021-12-11 06:00 | 44541.25 |  | 53.4%
2021-12-11 07:00 | 44541.2917 |  | 54.35%
2021-12-11 08:00 | 44541.3333 |  | 56.18%
2021-12-11 09:00 | 44541.375 |  | 57.94%
2021-12-11 10:00 | 44541.4167 |  | 59.14%
2021-12-11 11:00 | 44541.4583 |  | 59.37%
2021-12-11 12:00 | 44541.5 |  | 59.95%
2021-12-11 13:00 | 44541.5417 |  | 59.77%
2021-12-11 14:00 | 44541.5833 |  | 60.16%
2021-12-11 15:00 | 44541.625 |  | 59.99%
2021-12-11 16:00 | 44541.6667 |  | 59.84%
2021-12-11 17:00 | 44541.7083 |  | 59.14%
2021-12-11 18:00 | 44541.75 |  | 56.16%
2021-12-11 19:00 | 44541.7917 |  | 54.52%
2021-12-11 20:00 | 44541.8333 |  | 53.22%
2021-12-11 21:00 | 44541.875 |  | 51.85%
2021-12-11 22:00 | 44541.9167 |  | 51.63%
2021-12-11 23:00 | 44541.9583 |  | 53.51%
2021-12-12 | 44542 |  | 53.87%
2021-12-12 01:00 | 44542.0417 |  | 54.68%
2021-12-12 02:00 | 44542.0833 |  | 54.28%
2021-12-12 03:00 | 44542.125 |  | 53.59%
2021-12-12 04:00 | 44542.1667 |  | 52.43%
2021-12-12 05:00 | 44542.2083 |  | 52.11%
2021-12-12 06:00 | 44542.25 |  | 53%
2021-12-12 07:00 | 44542.2917 |  | 53.94%
2021-12-12 08:00 | 44542.3333 |  | 55.76%
2021-12-12 09:00 | 44542.375 |  | 57.5%
2021-12-12 10:00 | 44542.4167 |  | 58.69%
2021-12-12 11:00 | 44542.4583 |  | 58.92%
2021-12-12 12:00 | 44542.5 |  | 59.5%
2021-12-12 13:00 | 44542.5417 |  | 59.32%
2021-12-12 14:00 | 44542.5833 |  | 59.7%
2021-12-12 15:00 | 44542.625 |  | 59.53%
2021-12-12 16:00 | 44542.6667 |  | 59.39%
2021-12-12 17:00 | 44542.7083 |  | 58.68%
2021-12-12 18:00 | 44542.75 |  | 55.73%
2021-12-12 19:00 | 44542.7917 |  | 54.11%
2021-12-12 20:00 | 44542.8333 |  | 52.82%
2021-12-12 21:00 | 44542.875 |  | 51.46%
2021-12-12 22:00 | 44542.9167 |  | 51.24%
2021-12-12 23:00 | 44542.9583 |  | 53.1%
2021-12-13 | 44543 |  | 55.01%
2021-12-13 01:00 | 44543.0417 |  | 54.8%
2021-12-13 02:00 | 44543.0833 |  | 54.61%
2021-12-13 03:00 | 44543.125 |  | 54.48%
2021-12-13 04:00 | 44543.1667 |  | 53.84%
2021-12-13 05:00 | 44543.2083 |  | 54.1%
2021-12-13 06:00 | 44543.25 |  | 55.63%
2021-12-13 07:00 | 44543.2917 |  | 58.34%
2021-12-13 08:00 | 44543.3333 |  | 59.75%
2021-12-13 09:00 | 44543.375 |  | 59.79%
2021-12-13 10:00 | 44543.4167 |  | 60.01%
2021-12-13 11:00 | 44543.4583 |  | 60%
2021-12-13 12:00 | 44543.5 |  | 60.29%
2021-12-13 13:00 | 44543.5417 |  | 60.42%
2021-12-13 14:00 | 44543.5833 |  | 60.5%
2021-12-13 15:00 | 44543.625 |  | 60.7%
2021-12-13 16:00 | 44543.6667 |  | 60.94%
2021-12-13 17:00 | 44543.7083 |  | 60.75%
2021-12-13 18:00 | 44543.75 |  | 60.68%
2021-12-13 19:00 | 44543.7917 |  | 59.59%
2021-12-13 20:00 | 44543.8333 |  | 58.35%
2021-12-13 21:00 | 44543.875 |  | 56.37%
2021-12-13 22:00 | 44543.9167 |  | 54.95%
2021-12-13 23:00 | 44543.9583 |  | 55.37%
2021-12-14 | 44544 |  | 54.54%
2021-12-14 01:00 | 44544.0417 |  | 54.33%
2021-12-14 02:00 | 44544.0833 |  | 54.15%
2021-12-14 03:00 | 44544.125 |  | 54.02%
2021-12-14 04:00 | 44544.1667 |  | 53.38%
2021-12-14 05:00 | 44544.2083 |  | 53.64%
2021-12-14 06:00 | 44544.25 |  | 55.15%
2021-12-14 07:00 | 44544.2917 |  | 57.84%
2021-12-14 08:00 | 44544.3333 |  | 59.24%
2021-12-14 09:00 | 44544.375 |  | 59.28%
2021-12-14 10:00 | 44544.4167 |  | 59.5%
2021-12-14 11:00 | 44544.4583 |  | 59.49%
2021-12-14 12:00 | 44544.5 |  | 59.78%
2021-12-14 13:00 | 44544.5417 |  | 59.9%
2021-12-14 14:00 | 44544.5833 |  | 59.99%
2021-12-14 15:00 | 44544.625 |  | 60.19%
2021-12-14 16:00 | 44544.6667 |  | 60.43%
2021-12-14 17:00 | 44544.7083 |  | 60.24%
2021-12-14 18:00 | 44544.75 |  | 60.17%
2021-12-14 19:00 | 44544.7917 |  | 59.09%
2021-12-14 20:00 | 44544.8333 |  | 57.86%
2021-12-14 21:00 | 44544.875 |  | 55.9%
2021-12-14 22:00 | 44544.9167 |  | 54.48%
2021-12-14 23:00 | 44544.9583 |  | 54.9%
2021-12-15 | 44545 |  | 54.53%
2021-12-15 01:00 | 44545.0417 |  | 54.32%
2021-12-15 02:00 | 44545.0833 |  | 54.14%
2021-12-15 03:00 | 44545.125 |  | 54.01%
2021-12-15 04:00 | 44545.1667 |  | 53.37%
2021-12-15 05:00 | 44545.2083 |  | 53.63%
2021-12-15 06:00 | 44545.25 |  | 55.14%
2021-12-15 07:00 | 44545.2917 |  | 57.83%
2021-12-15 08:00 | 44545.3333 |  | 59.23%
2021-12-15 09:00 | 44545.375 |  | 59.27%
2021-12-15 10:00 | 44545.4167 |  | 59.48%
2021-12-15 11:00 | 44545.4583 |  | 59.48%
2021-12-15 12:00 | 44545.5 |  | 59.77%
2021-12-15 13:00 | 44545.5417 |  | 59.89%
2021-12-15 14:00 | 44545.5833 |  | 59.97%
2021-12-15 15:00 | 44545.625 |  | 60.17%
2021-12-15 16:00 | 44545.6667 |  | 60.41%
2021-12-15 17:00 | 44545.7083 |  | 60.22%
2021-12-15 18:00 | 44545.75 |  | 60.15%
2021-12-15 19:00 | 44545.7917 |  | 59.07%
2021-12-15 20:00 | 44545.8333 |  | 57.85%
2021-12-15 21:00 | 44545.875 |  | 55.88%
2021-12-15 22:00 | 44545.9167 |  | 54.47%
2021-12-15 23:00 | 44545.9583 |  | 54.89%
2021-12-16 | 44546 |  | 55.13%
2021-12-16 01:00 | 44546.0417 |  | 54.92%
2021-12-16 02:00 | 44546.0833 |  | 54.73%
2021-12-16 03:00 | 44546.125 |  | 54.6%
2021-12-16 04:00 | 44546.1667 |  | 53.96%
2021-12-16 05:00 | 44546.2083 |  | 54.22%
2021-12-16 06:00 | 44546.25 |  | 55.75%
2021-12-16 07:00 | 44546.2917 |  | 58.46%
2021-12-16 08:00 | 44546.3333 |  | 59.88%
2021-12-16 09:00 | 44546.375 |  | 59.92%
2021-12-16 10:00 | 44546.4167 |  | 60.14%
2021-12-16 11:00 | 44546.4583 |  | 60.14%
2021-12-16 12:00 | 44546.5 |  | 60.43%
2021-12-16 13:00 | 44546.5417 |  | 60.55%
2021-12-16 14:00 | 44546.5833 |  | 60.63%
2021-12-16 15:00 | 44546.625 |  | 60.84%
2021-12-16 16:00 | 44546.6667 |  | 61.08%
2021-12-16 17:00 | 44546.7083 |  | 60.88%
2021-12-16 18:00 | 44546.75 |  | 60.82%
2021-12-16 19:00 | 44546.7917 |  | 59.72%
2021-12-16 20:00 | 44546.8333 |  | 58.48%
2021-12-16 21:00 | 44546.875 |  | 56.5%
2021-12-16 22:00 | 44546.9167 |  | 55.07%
2021-12-16 23:00 | 44546.9583 |  | 55.49%
2021-12-17 | 44547 |  | 55.06%
2021-12-17 01:00 | 44547.0417 |  | 54.85%
2021-12-17 02:00 | 44547.0833 |  | 54.67%
2021-12-17 03:00 | 44547.125 |  | 54.54%
2021-12-17 04:00 | 44547.1667 |  | 53.89%
2021-12-17 05:00 | 44547.2083 |  | 54.15%
2021-12-17 06:00 | 44547.25 |  | 55.68%
2021-12-17 07:00 | 44547.2917 |  | 58.39%
2021-12-17 08:00 | 44547.3333 |  | 59.81%
2021-12-17 09:00 | 44547.375 |  | 59.85%
2021-12-17 10:00 | 44547.4167 |  | 60.06%
2021-12-17 11:00 | 44547.4583 |  | 60.06%
2021-12-17 12:00 | 44547.5 |  | 60.35%
2021-12-17 13:00 | 44547.5417 |  | 60.47%
2021-12-17 14:00 | 44547.5833 |  | 60.56%
2021-12-17 15:00 | 44547.625 |  | 60.76%
2021-12-17 16:00 | 44547.6667 |  | 61%
2021-12-17 17:00 | 44547.7083 |  | 60.81%
2021-12-17 18:00 | 44547.75 |  | 60.74%
2021-12-17 19:00 | 44547.7917 |  | 59.65%
2021-12-17 20:00 | 44547.8333 |  | 58.41%
2021-12-17 21:00 | 44547.875 |  | 56.43%
2021-12-17 22:00 | 44547.9167 |  | 55%
2021-12-17 23:00 | 44547.9583 |  | 55.42%
2021-12-18 | 44548 |  | 53.33%
2021-12-18 01:00 | 44548.0417 |  | 54.13%
2021-12-18 02:00 | 44548.0833 |  | 53.73%
2021-12-18 03:00 | 44548.125 |  | 53.05%
2021-12-18 04:00 | 44548.1667 |  | 51.91%
2021-12-18 05:00 | 44548.2083 |  | 51.58%
2021-12-18 06:00 | 44548.25 |  | 52.46%
2021-12-18 07:00 | 44548.2917 |  | 53.39%
2021-12-18 08:00 | 44548.3333 |  | 55.2%
2021-12-18 09:00 | 44548.375 |  | 56.92%
2021-12-18 10:00 | 44548.4167 |  | 58.1%
2021-12-18 11:00 | 44548.4583 |  | 58.33%
2021-12-18 12:00 | 44548.5 |  | 58.9%
2021-12-18 13:00 | 44548.5417 |  | 58.72%
2021-12-18 14:00 | 44548.5833 |  | 59.1%
2021-12-18 15:00 | 44548.625 |  | 58.94%
2021-12-18 16:00 | 44548.6667 |  | 58.79%
2021-12-18 17:00 | 44548.7083 |  | 58.1%
2021-12-18 18:00 | 44548.75 |  | 55.17%
2021-12-18 19:00 | 44548.7917 |  | 53.56%
2021-12-18 20:00 | 44548.8333 |  | 52.29%
2021-12-18 21:00 | 44548.875 |  | 50.94%
2021-12-18 22:00 | 44548.9167 |  | 50.72%
2021-12-18 23:00 | 44548.9583 |  | 52.57%
2021-12-19 | 44549 |  | 53.51%
2021-12-19 01:00 | 44549.0417 |  | 54.31%
2021-12-19 02:00 | 44549.0833 |  | 53.91%
2021-12-19 03:00 | 44549.125 |  | 53.23%
2021-12-19 04:00 | 44549.1667 |  | 52.08%
2021-12-19 05:00 | 44549.2083 |  | 51.76%
2021-12-19 06:00 | 44549.25 |  | 52.64%
2021-12-19 07:00 | 44549.2917 |  | 53.57%
2021-12-19 08:00 | 44549.3333 |  | 55.38%
2021-12-19 09:00 | 44549.375 |  | 57.11%
2021-12-19 10:00 | 44549.4167 |  | 58.3%
2021-12-19 11:00 | 44549.4583 |  | 58.52%
2021-12-19 12:00 | 44549.5 |  | 59.09%
2021-12-19 13:00 | 44549.5417 |  | 58.92%
2021-12-19 14:00 | 44549.5833 |  | 59.3%
2021-12-19 15:00 | 44549.625 |  | 59.13%
2021-12-19 16:00 | 44549.6667 |  | 58.99%
2021-12-19 17:00 | 44549.7083 |  | 58.29%
2021-12-19 18:00 | 44549.75 |  | 55.36%
2021-12-19 19:00 | 44549.7917 |  | 53.74%
2021-12-19 20:00 | 44549.8333 |  | 52.46%
2021-12-19 21:00 | 44549.875 |  | 51.11%
2021-12-19 22:00 | 44549.9167 |  | 50.89%
2021-12-19 23:00 | 44549.9583 |  | 52.75%
2021-12-20 | 44550 |  | 54.52%
2021-12-20 01:00 | 44550.0417 |  | 54.31%
2021-12-20 02:00 | 44550.0833 |  | 54.12%
2021-12-20 03:00 | 44550.125 |  | 54%
2021-12-20 04:00 | 44550.1667 |  | 53.36%
2021-12-20 05:00 | 44550.2083 |  | 53.62%
2021-12-20 06:00 | 44550.25 |  | 55.13%
2021-12-20 07:00 | 44550.2917 |  | 57.81%
2021-12-20 08:00 | 44550.3333 |  | 59.21%
2021-12-20 09:00 | 44550.375 |  | 59.25%
2021-12-20 10:00 | 44550.4167 |  | 59.47%
2021-12-20 11:00 | 44550.4583 |  | 59.47%
2021-12-20 12:00 | 44550.5 |  | 59.75%
2021-12-20 13:00 | 44550.5417 |  | 59.87%
2021-12-20 14:00 | 44550.5833 |  | 59.96%
2021-12-20 15:00 | 44550.625 |  | 60.16%
2021-12-20 16:00 | 44550.6667 |  | 60.4%
2021-12-20 17:00 | 44550.7083 |  | 60.21%
2021-12-20 18:00 | 44550.75 |  | 60.14%
2021-12-20 19:00 | 44550.7917 |  | 59.06%
2021-12-20 20:00 | 44550.8333 |  | 57.83%
2021-12-20 21:00 | 44550.875 |  | 55.87%
2021-12-20 22:00 | 44550.9167 |  | 54.45%
2021-12-20 23:00 | 44550.9583 |  | 54.87%
2021-12-21 | 44551 |  | 54.98%
2021-12-21 01:00 | 44551.0417 |  | 54.77%
2021-12-21 02:00 | 44551.0833 |  | 54.59%
2021-12-21 03:00 | 44551.125 |  | 54.46%
2021-12-21 04:00 | 44551.1667 |  | 53.81%
2021-12-21 05:00 | 44551.2083 |  | 54.08%
2021-12-21 06:00 | 44551.25 |  | 55.6%
2021-12-21 07:00 | 44551.2917 |  | 58.31%
2021-12-21 08:00 | 44551.3333 |  | 59.72%
2021-12-21 09:00 | 44551.375 |  | 59.76%
2021-12-21 10:00 | 44551.4167 |  | 59.98%
2021-12-21 11:00 | 44551.4583 |  | 59.97%
2021-12-21 12:00 | 44551.5 |  | 60.26%
2021-12-21 13:00 | 44551.5417 |  | 60.39%
2021-12-21 14:00 | 44551.5833 |  | 60.47%
2021-12-21 15:00 | 44551.625 |  | 60.67%
2021-12-21 16:00 | 44551.6667 |  | 60.91%
2021-12-21 17:00 | 44551.7083 |  | 60.72%
2021-12-21 18:00 | 44551.75 |  | 60.65%
2021-12-21 19:00 | 44551.7917 |  | 59.56%
2021-12-21 20:00 | 44551.8333 |  | 58.33%
2021-12-21 21:00 | 44551.875 |  | 56.35%
2021-12-21 22:00 | 44551.9167 |  | 54.92%
2021-12-21 23:00 | 44551.9583 |  | 55.34%
2021-12-22 | 44552 |  | 54.98%
2021-12-22 01:00 | 44552.0417 |  | 54.77%
2021-12-22 02:00 | 44552.0833 |  | 54.59%
2021-12-22 03:00 | 44552.125 |  | 54.46%
2021-12-22 04:00 | 44552.1667 |  | 53.81%
2021-12-22 05:00 | 44552.2083 |  | 54.08%
2021-12-22 06:00 | 44552.25 |  | 55.6%
2021-12-22 07:00 | 44552.2917 |  | 58.31%
2021-12-22 08:00 | 44552.3333 |  | 59.72%
2021-12-22 09:00 | 44552.375 |  | 59.76%
2021-12-22 10:00 | 44552.4167 |  | 59.98%
2021-12-22 11:00 | 44552.4583 |  | 59.97%
2021-12-22 12:00 | 44552.5 |  | 60.26%
2021-12-22 13:00 | 44552.5417 |  | 60.39%
2021-12-22 14:00 | 44552.5833 |  | 60.47%
2021-12-22 15:00 | 44552.625 |  | 60.67%
2021-12-22 16:00 | 44552.6667 |  | 60.91%
2021-12-22 17:00 | 44552.7083 |  | 60.72%
2021-12-22 18:00 | 44552.75 |  | 60.65%
2021-12-22 19:00 | 44552.7917 |  | 59.56%
2021-12-22 20:00 | 44552.8333 |  | 58.33%
2021-12-22 21:00 | 44552.875 |  | 56.35%
2021-12-22 22:00 | 44552.9167 |  | 54.92%
2021-12-22 23:00 | 44552.9583 |  | 55.34%
2021-12-23 | 44553 |  | 55.35%
2021-12-23 01:00 | 44553.0417 |  | 55.14%
2021-12-23 02:00 | 44553.0833 |  | 54.95%
2021-12-23 03:00 | 44553.125 |  | 54.82%
2021-12-23 04:00 | 44553.1667 |  | 54.18%
2021-12-23 05:00 | 44553.2083 |  | 54.44%
2021-12-23 06:00 | 44553.25 |  | 55.97%
2021-12-23 07:00 | 44553.2917 |  | 58.7%
2021-12-23 08:00 | 44553.3333 |  | 60.12%
2021-12-23 09:00 | 44553.375 |  | 60.16%
2021-12-23 10:00 | 44553.4167 |  | 60.38%
2021-12-23 11:00 | 44553.4583 |  | 60.38%
2021-12-23 12:00 | 44553.5 |  | 60.67%
2021-12-23 13:00 | 44553.5417 |  | 60.79%
2021-12-23 14:00 | 44553.5833 |  | 60.88%
2021-12-23 15:00 | 44553.625 |  | 61.08%
2021-12-23 16:00 | 44553.6667 |  | 61.33%
2021-12-23 17:00 | 44553.7083 |  | 61.13%
2021-12-23 18:00 | 44553.75 |  | 61.06%
2021-12-23 19:00 | 44553.7917 |  | 59.96%
2021-12-23 20:00 | 44553.8333 |  | 58.72%
2021-12-23 21:00 | 44553.875 |  | 56.73%
2021-12-23 22:00 | 44553.9167 |  | 55.29%
2021-12-23 23:00 | 44553.9583 |  | 55.72%
2021-12-24 | 44554 |  | 55.71%
2021-12-24 01:00 | 44554.0417 |  | 55.49%
2021-12-24 02:00 | 44554.0833 |  | 55.3%
2021-12-24 03:00 | 44554.125 |  | 55.17%
2021-12-24 04:00 | 44554.1667 |  | 54.52%
2021-12-24 05:00 | 44554.2083 |  | 54.79%
2021-12-24 06:00 | 44554.25 |  | 56.33%
2021-12-24 07:00 | 44554.2917 |  | 59.07%
2021-12-24 08:00 | 44554.3333 |  | 60.5%
2021-12-24 09:00 | 44554.375 |  | 60.55%
2021-12-24 10:00 | 44554.4167 |  | 60.76%
2021-12-24 11:00 | 44554.4583 |  | 60.76%
2021-12-24 12:00 | 44554.5 |  | 61.06%
2021-12-24 13:00 | 44554.5417 |  | 61.18%
2021-12-24 14:00 | 44554.5833 |  | 61.27%
2021-12-24 15:00 | 44554.625 |  | 61.47%
2021-12-24 16:00 | 44554.6667 |  | 61.72%
2021-12-24 17:00 | 44554.7083 |  | 61.52%
2021-12-24 18:00 | 44554.75 |  | 61.45%
2021-12-24 19:00 | 44554.7917 |  | 60.34%
2021-12-24 20:00 | 44554.8333 |  | 59.09%
2021-12-24 21:00 | 44554.875 |  | 57.09%
2021-12-24 22:00 | 44554.9167 |  | 55.64%
2021-12-24 23:00 | 44554.9583 |  | 56.07%
2021-12-25 | 44555 |  | 53.49%
2021-12-25 01:00 | 44555.0417 |  | 54.28%
2021-12-25 02:00 | 44555.0833 |  | 53.89%
2021-12-25 03:00 | 44555.125 |  | 53.2%
2021-12-25 04:00 | 44555.1667 |  | 52.06%
2021-12-25 05:00 | 44555.2083 |  | 51.73%
2021-12-25 06:00 | 44555.25 |  | 52.62%
2021-12-25 07:00 | 44555.2917 |  | 53.55%
2021-12-25 08:00 | 44555.3333 |  | 55.36%
2021-12-25 09:00 | 44555.375 |  | 57.09%
2021-12-25 10:00 | 44555.4167 |  | 58.27%
2021-12-25 11:00 | 44555.4583 |  | 58.5%
2021-12-25 12:00 | 44555.5 |  | 59.07%
2021-12-25 13:00 | 44555.5417 |  | 58.89%
2021-12-25 14:00 | 44555.5833 |  | 59.27%
2021-12-25 15:00 | 44555.625 |  | 59.11%
2021-12-25 16:00 | 44555.6667 |  | 58.96%
2021-12-25 17:00 | 44555.7083 |  | 58.26%
2021-12-25 18:00 | 44555.75 |  | 55.33%
2021-12-25 19:00 | 44555.7917 |  | 53.72%
2021-12-25 20:00 | 44555.8333 |  | 52.44%
2021-12-25 21:00 | 44555.875 |  | 51.09%
2021-12-25 22:00 | 44555.9167 |  | 50.87%
2021-12-25 23:00 | 44555.9583 |  | 52.72%
2021-12-26 | 44556 |  | 54.5%
2021-12-26 01:00 | 44556.0417 |  | 55.32%
2021-12-26 02:00 | 44556.0833 |  | 54.91%
2021-12-26 03:00 | 44556.125 |  | 54.21%
2021-12-26 04:00 | 44556.1667 |  | 53.05%
2021-12-26 05:00 | 44556.2083 |  | 52.72%
2021-12-26 06:00 | 44556.25 |  | 53.62%
2021-12-26 07:00 | 44556.2917 |  | 54.57%
2021-12-26 08:00 | 44556.3333 |  | 56.41%
2021-12-26 09:00 | 44556.375 |  | 58.17%
2021-12-26 10:00 | 44556.4167 |  | 59.38%
2021-12-26 11:00 | 44556.4583 |  | 59.61%
2021-12-26 12:00 | 44556.5 |  | 60.19%
2021-12-26 13:00 | 44556.5417 |  | 60.01%
2021-12-26 14:00 | 44556.5833 |  | 60.4%
2021-12-26 15:00 | 44556.625 |  | 60.23%
2021-12-26 16:00 | 44556.6667 |  | 60.08%
2021-12-26 17:00 | 44556.7083 |  | 59.37%
2021-12-26 18:00 | 44556.75 |  | 56.38%
2021-12-26 19:00 | 44556.7917 |  | 54.74%
2021-12-26 20:00 | 44556.8333 |  | 53.43%
2021-12-26 21:00 | 44556.875 |  | 52.06%
2021-12-26 22:00 | 44556.9167 |  | 51.84%
2021-12-26 23:00 | 44556.9583 |  | 53.72%
2021-12-27 | 44557 |  | 55.71%
2021-12-27 01:00 | 44557.0417 |  | 55.49%
2021-12-27 02:00 | 44557.0833 |  | 55.3%
2021-12-27 03:00 | 44557.125 |  | 55.17%
2021-12-27 04:00 | 44557.1667 |  | 54.52%
2021-12-27 05:00 | 44557.2083 |  | 54.79%
2021-12-27 06:00 | 44557.25 |  | 56.33%
2021-12-27 07:00 | 44557.2917 |  | 59.07%
2021-12-27 08:00 | 44557.3333 |  | 60.5%
2021-12-27 09:00 | 44557.375 |  | 60.55%
2021-12-27 10:00 | 44557.4167 |  | 60.76%
2021-12-27 11:00 | 44557.4583 |  | 60.76%
2021-12-27 12:00 | 44557.5 |  | 61.06%
2021-12-27 13:00 | 44557.5417 |  | 61.18%
2021-12-27 14:00 | 44557.5833 |  | 61.27%
2021-12-27 15:00 | 44557.625 |  | 61.47%
2021-12-27 16:00 | 44557.6667 |  | 61.72%
2021-12-27 17:00 | 44557.7083 |  | 61.52%
2021-12-27 18:00 | 44557.75 |  | 61.45%
2021-12-27 19:00 | 44557.7917 |  | 60.34%
2021-12-27 20:00 | 44557.8333 |  | 59.09%
2021-12-27 21:00 | 44557.875 |  | 57.09%
2021-12-27 22:00 | 44557.9167 |  | 55.64%
2021-12-27 23:00 | 44557.9583 |  | 56.07%
2021-12-28 | 44558 |  | 55.71%
2021-12-28 01:00 | 44558.0417 |  | 55.49%
2021-12-28 02:00 | 44558.0833 |  | 55.3%
2021-12-28 03:00 | 44558.125 |  | 55.17%
2021-12-28 04:00 | 44558.1667 |  | 54.52%
2021-12-28 05:00 | 44558.2083 |  | 54.79%
2021-12-28 06:00 | 44558.25 |  | 56.33%
2021-12-28 07:00 | 44558.2917 |  | 59.07%
2021-12-28 08:00 | 44558.3333 |  | 60.5%
2021-12-28 09:00 | 44558.375 |  | 60.55%
2021-12-28 10:00 | 44558.4167 |  | 60.76%
2021-12-28 11:00 | 44558.4583 |  | 60.76%
2021-12-28 12:00 | 44558.5 |  | 61.06%
2021-12-28 13:00 | 44558.5417 |  | 61.18%
2021-12-28 14:00 | 44558.5833 |  | 61.27%
2021-12-28 15:00 | 44558.625 |  | 61.47%
2021-12-28 16:00 | 44558.6667 |  | 61.72%
2021-12-28 17:00 | 44558.7083 |  | 61.52%
2021-12-28 18:00 | 44558.75 |  | 61.45%
2021-12-28 19:00 | 44558.7917 |  | 60.34%
2021-12-28 20:00 | 44558.8333 |  | 59.09%
2021-12-28 21:00 | 44558.875 |  | 57.09%
2021-12-28 22:00 | 44558.9167 |  | 55.64%
2021-12-28 23:00 | 44558.9583 |  | 56.07%
2021-12-29 | 44559 |  | 55.71%
2021-12-29 01:00 | 44559.0417 |  | 55.49%
2021-12-29 02:00 | 44559.0833 |  | 55.3%
2021-12-29 03:00 | 44559.125 |  | 55.17%
2021-12-29 04:00 | 44559.1667 |  | 54.52%
2021-12-29 05:00 | 44559.2083 |  | 54.79%
2021-12-29 06:00 | 44559.25 |  | 56.33%
2021-12-29 07:00 | 44559.2917 |  | 59.07%
2021-12-29 08:00 | 44559.3333 |  | 60.5%
2021-12-29 09:00 | 44559.375 |  | 60.55%
2021-12-29 10:00 | 44559.4167 |  | 60.76%
2021-12-29 11:00 | 44559.4583 |  | 60.76%
2021-12-29 12:00 | 44559.5 |  | 61.06%
2021-12-29 13:00 | 44559.5417 |  | 61.18%
2021-12-29 14:00 | 44559.5833 |  | 61.27%
2021-12-29 15:00 | 44559.625 |  | 61.47%
2021-12-29 16:00 | 44559.6667 |  | 61.72%
2021-12-29 17:00 | 44559.7083 |  | 61.52%
2021-12-29 18:00 | 44559.75 |  | 61.45%
2021-12-29 19:00 | 44559.7917 |  | 60.34%
2021-12-29 20:00 | 44559.8333 |  | 59.09%
2021-12-29 21:00 | 44559.875 |  | 57.09%
2021-12-29 22:00 | 44559.9167 |  | 55.64%
2021-12-29 23:00 | 44559.9583 |  | 56.07%
2021-12-30 | 44560 |  | 55.71%
2021-12-30 01:00 | 44560.0417 |  | 55.49%
2021-12-30 02:00 | 44560.0833 |  | 55.3%
2021-12-30 03:00 | 44560.125 |  | 55.17%
2021-12-30 04:00 | 44560.1667 |  | 54.52%
2021-12-30 05:00 | 44560.2083 |  | 54.79%
2021-12-30 06:00 | 44560.25 |  | 56.33%
2021-12-30 07:00 | 44560.2917 |  | 59.07%
2021-12-30 08:00 | 44560.3333 |  | 60.5%
2021-12-30 09:00 | 44560.375 |  | 60.55%
2021-12-30 10:00 | 44560.4167 |  | 60.76%
2021-12-30 11:00 | 44560.4583 |  | 60.76%
2021-12-30 12:00 | 44560.5 |  | 61.06%
2021-12-30 13:00 | 44560.5417 |  | 61.18%
2021-12-30 14:00 | 44560.5833 |  | 61.27%
2021-12-30 15:00 | 44560.625 |  | 61.47%
2021-12-30 16:00 | 44560.6667 |  | 61.72%
2021-12-30 17:00 | 44560.7083 |  | 61.52%
2021-12-30 18:00 | 44560.75 |  | 61.45%
2021-12-30 19:00 | 44560.7917 |  | 60.34%
2021-12-30 20:00 | 44560.8333 |  | 59.09%
2021-12-30 21:00 | 44560.875 |  | 57.09%
2021-12-30 22:00 | 44560.9167 |  | 55.64%
2021-12-30 23:00 | 44560.9583 |  | 56.07%
2021-12-31 | 44561 |  | 55.75%
2021-12-31 01:00 | 44561.0417 |  | 55.53%
2021-12-31 02:00 | 44561.0833 |  | 55.34%
2021-12-31 03:00 | 44561.125 |  | 55.21%
2021-12-31 04:00 | 44561.1667 |  | 54.56%
2021-12-31 05:00 | 44561.2083 |  | 54.83%
2021-12-31 06:00 | 44561.25 |  | 56.37%
2021-12-31 07:00 | 44561.2917 |  | 59.12%
2021-12-31 08:00 | 44561.3333 |  | 60.55%
2021-12-31 09:00 | 44561.375 |  | 60.59%
2021-12-31 10:00 | 44561.4167 |  | 60.81%
2021-12-31 11:00 | 44561.4583 |  | 60.81%
2021-12-31 12:00 | 44561.5 |  | 61.1%
2021-12-31 13:00 | 44561.5417 |  | 61.22%
2021-12-31 14:00 | 44561.5833 |  | 61.31%
2021-12-31 15:00 | 44561.625 |  | 61.52%
2021-12-31 16:00 | 44561.6667 |  | 61.76%
2021-12-31 17:00 | 44561.7083 |  | 61.56%
2021-12-31 18:00 | 44561.75 |  | 61.5%
2021-12-31 19:00 | 44561.7917 |  | 60.39%
2021-12-31 20:00 | 44561.8333 |  | 59.14%
2021-12-31 21:00 | 44561.875 |  | 57.13%
2021-12-31 22:00 | 44561.9167 |  | 55.68%
2021-12-31 23:00 | 44561.9583 |  | 56.11%
2022-01-01 | 44562 |  | 51.77%
2022-01-01 01:00 | 44562.0417 |  | 51.25%
2022-01-01 02:00 | 44562.0833 |  | 51.15%
2022-01-01 03:00 | 44562.125 |  | 51%
2022-01-01 04:00 | 44562.1667 |  | 50.94%
2022-01-01 05:00 | 44562.2083 |  | 50.8%
2022-01-01 06:00 | 44562.25 |  | 51.23%
2022-01-01 07:00 | 44562.2917 |  | 51.92%
2022-01-01 08:00 | 44562.3333 |  | 53.14%
2022-01-01 09:00 | 44562.375 |  | 54.02%
2022-01-01 10:00 | 44562.4167 |  | 54.77%
2022-01-01 11:00 | 44562.4583 |  | 55%
2022-01-01 12:00 | 44562.5 |  | 55.02%
2022-01-01 13:00 | 44562.5417 |  | 54.54%
2022-01-01 14:00 | 44562.5833 |  | 54.52%
2022-01-01 15:00 | 44562.625 |  | 54.5%
2022-01-01 16:00 | 44562.6667 |  | 54.4%
2022-01-01 17:00 | 44562.7083 |  | 54.27%
2022-01-01 18:00 | 44562.75 |  | 53.74%
2022-01-01 19:00 | 44562.7917 |  | 53.03%
2022-01-01 20:00 | 44562.8333 |  | 52.4%
2022-01-01 21:00 | 44562.875 |  | 52.63%
2022-01-01 22:00 | 44562.9167 |  | 52.5%
2022-01-01 23:00 | 44562.9583 |  | 52.82%
2022-01-02 | 44563 |  | 51.59%
2022-01-02 01:00 | 44563.0417 |  | 51.08%
2022-01-02 02:00 | 44563.0833 |  | 50.97%
2022-01-02 03:00 | 44563.125 |  | 50.82%
2022-01-02 04:00 | 44563.1667 |  | 50.76%
2022-01-02 05:00 | 44563.2083 |  | 50.63%
2022-01-02 06:00 | 44563.25 |  | 51.05%
2022-01-02 07:00 | 44563.2917 |  | 51.74%
2022-01-02 08:00 | 44563.3333 |  | 52.96%
2022-01-02 09:00 | 44563.375 |  | 53.83%
2022-01-02 10:00 | 44563.4167 |  | 54.58%
2022-01-02 11:00 | 44563.4583 |  | 54.81%
2022-01-02 12:00 | 44563.5 |  | 54.83%
2022-01-02 13:00 | 44563.5417 |  | 54.36%
2022-01-02 14:00 | 44563.5833 |  | 54.33%
2022-01-02 15:00 | 44563.625 |  | 54.31%
2022-01-02 16:00 | 44563.6667 |  | 54.21%
2022-01-02 17:00 | 44563.7083 |  | 54.08%
2022-01-02 18:00 | 44563.75 |  | 53.55%
2022-01-02 19:00 | 44563.7917 |  | 52.84%
2022-01-02 20:00 | 44563.8333 |  | 52.22%
2022-01-02 21:00 | 44563.875 |  | 52.44%
2022-01-02 22:00 | 44563.9167 |  | 52.31%
2022-01-02 23:00 | 44563.9583 |  | 52.64%
2022-01-03 | 44564 |  | 52.44%
2022-01-03 01:00 | 44564.0417 |  | 51.77%
2022-01-03 02:00 | 44564.0833 |  | 51.4%
2022-01-03 03:00 | 44564.125 |  | 51.2%
2022-01-03 04:00 | 44564.1667 |  | 50.93%
2022-01-03 05:00 | 44564.2083 |  | 50.76%
2022-01-03 06:00 | 44564.25 |  | 52.03%
2022-01-03 07:00 | 44564.2917 |  | 54.08%
2022-01-03 08:00 | 44564.3333 |  | 54.67%
2022-01-03 09:00 | 44564.375 |  | 53.88%
2022-01-03 10:00 | 44564.4167 |  | 53.4%
2022-01-03 11:00 | 44564.4583 |  | 53.74%
2022-01-03 12:00 | 44564.5 |  | 53.69%
2022-01-03 13:00 | 44564.5417 |  | 53.61%
2022-01-03 14:00 | 44564.5833 |  | 54.08%
2022-01-03 15:00 | 44564.625 |  | 54.47%
2022-01-03 16:00 | 44564.6667 |  | 54.47%
2022-01-03 17:00 | 44564.7083 |  | 54.3%
2022-01-03 18:00 | 44564.75 |  | 54.05%
2022-01-03 19:00 | 44564.7917 |  | 53.67%
2022-01-03 20:00 | 44564.8333 |  | 53.05%
2022-01-03 21:00 | 44564.875 |  | 53.14%
2022-01-03 22:00 | 44564.9167 |  | 52.79%
2022-01-03 23:00 | 44564.9583 |  | 53.18%
2022-01-04 | 44565 |  | 52.24%
2022-01-04 01:00 | 44565.0417 |  | 51.57%
2022-01-04 02:00 | 44565.0833 |  | 51.19%
2022-01-04 03:00 | 44565.125 |  | 51%
2022-01-04 04:00 | 44565.1667 |  | 50.73%
2022-01-04 05:00 | 44565.2083 |  | 50.56%
2022-01-04 06:00 | 44565.25 |  | 51.82%
2022-01-04 07:00 | 44565.2917 |  | 53.87%
2022-01-04 08:00 | 44565.3333 |  | 54.45%
2022-01-04 09:00 | 44565.375 |  | 53.66%
2022-01-04 10:00 | 44565.4167 |  | 53.19%
2022-01-04 11:00 | 44565.4583 |  | 53.53%
2022-01-04 12:00 | 44565.5 |  | 53.48%
2022-01-04 13:00 | 44565.5417 |  | 53.4%
2022-01-04 14:00 | 44565.5833 |  | 53.87%
2022-01-04 15:00 | 44565.625 |  | 54.25%
2022-01-04 16:00 | 44565.6667 |  | 54.25%
2022-01-04 17:00 | 44565.7083 |  | 54.09%
2022-01-04 18:00 | 44565.75 |  | 53.84%
2022-01-04 19:00 | 44565.7917 |  | 53.46%
2022-01-04 20:00 | 44565.8333 |  | 52.84%
2022-01-04 21:00 | 44565.875 |  | 52.93%
2022-01-04 22:00 | 44565.9167 |  | 52.58%
2022-01-04 23:00 | 44565.9583 |  | 52.97%
2022-01-05 | 44566 |  | 52.27%
2022-01-05 01:00 | 44566.0417 |  | 51.6%
2022-01-05 02:00 | 44566.0833 |  | 51.22%
2022-01-05 03:00 | 44566.125 |  | 51.03%
2022-01-05 04:00 | 44566.1667 |  | 50.76%
2022-01-05 05:00 | 44566.2083 |  | 50.59%
2022-01-05 06:00 | 44566.25 |  | 51.85%
2022-01-05 07:00 | 44566.2917 |  | 53.9%
2022-01-05 08:00 | 44566.3333 |  | 54.48%
2022-01-05 09:00 | 44566.375 |  | 53.7%
2022-01-05 10:00 | 44566.4167 |  | 53.22%
2022-01-05 11:00 | 44566.4583 |  | 53.56%
2022-01-05 12:00 | 44566.5 |  | 53.51%
2022-01-05 13:00 | 44566.5417 |  | 53.43%
2022-01-05 14:00 | 44566.5833 |  | 53.9%
2022-01-05 15:00 | 44566.625 |  | 54.29%
2022-01-05 16:00 | 44566.6667 |  | 54.29%
2022-01-05 17:00 | 44566.7083 |  | 54.12%
2022-01-05 18:00 | 44566.75 |  | 53.87%
2022-01-05 19:00 | 44566.7917 |  | 53.49%
2022-01-05 20:00 | 44566.8333 |  | 52.87%
2022-01-05 21:00 | 44566.875 |  | 52.96%
2022-01-05 22:00 | 44566.9167 |  | 52.62%
2022-01-05 23:00 | 44566.9583 |  | 53%
2022-01-06 | 44567 |  | 52.52%
2022-01-06 01:00 | 44567.0417 |  | 51.86%
2022-01-06 02:00 | 44567.0833 |  | 51.48%
2022-01-06 03:00 | 44567.125 |  | 51.28%
2022-01-06 04:00 | 44567.1667 |  | 51.01%
2022-01-06 05:00 | 44567.2083 |  | 50.84%
2022-01-06 06:00 | 44567.25 |  | 52.11%
2022-01-06 07:00 | 44567.2917 |  | 54.16%
2022-01-06 08:00 | 44567.3333 |  | 54.75%
2022-01-06 09:00 | 44567.375 |  | 53.96%
2022-01-06 10:00 | 44567.4167 |  | 53.48%
2022-01-06 11:00 | 44567.4583 |  | 53.82%
2022-01-06 12:00 | 44567.5 |  | 53.77%
2022-01-06 13:00 | 44567.5417 |  | 53.69%
2022-01-06 14:00 | 44567.5833 |  | 54.17%
2022-01-06 15:00 | 44567.625 |  | 54.55%
2022-01-06 16:00 | 44567.6667 |  | 54.55%
2022-01-06 17:00 | 44567.7083 |  | 54.38%
2022-01-06 18:00 | 44567.75 |  | 54.14%
2022-01-06 19:00 | 44567.7917 |  | 53.75%
2022-01-06 20:00 | 44567.8333 |  | 53.13%
2022-01-06 21:00 | 44567.875 |  | 53.22%
2022-01-06 22:00 | 44567.9167 |  | 52.87%
2022-01-06 23:00 | 44567.9583 |  | 53.26%
2022-01-07 | 44568 |  | 52.75%
2022-01-07 01:00 | 44568.0417 |  | 52.08%
2022-01-07 02:00 | 44568.0833 |  | 51.7%
2022-01-07 03:00 | 44568.125 |  | 51.5%
2022-01-07 04:00 | 44568.1667 |  | 51.23%
2022-01-07 05:00 | 44568.2083 |  | 51.05%
2022-01-07 06:00 | 44568.25 |  | 52.33%
2022-01-07 07:00 | 44568.2917 |  | 54.39%
2022-01-07 08:00 | 44568.3333 |  | 54.99%
2022-01-07 09:00 | 44568.375 |  | 54.19%
2022-01-07 10:00 | 44568.4167 |  | 53.71%
2022-01-07 11:00 | 44568.4583 |  | 54.05%
2022-01-07 12:00 | 44568.5 |  | 54%
2022-01-07 13:00 | 44568.5417 |  | 53.92%
2022-01-07 14:00 | 44568.5833 |  | 54.4%
2022-01-07 15:00 | 44568.625 |  | 54.79%
2022-01-07 16:00 | 44568.6667 |  | 54.78%
2022-01-07 17:00 | 44568.7083 |  | 54.62%
2022-01-07 18:00 | 44568.75 |  | 54.37%
2022-01-07 19:00 | 44568.7917 |  | 53.98%
2022-01-07 20:00 | 44568.8333 |  | 53.36%
2022-01-07 21:00 | 44568.875 |  | 53.45%
2022-01-07 22:00 | 44568.9167 |  | 53.1%
2022-01-07 23:00 | 44568.9583 |  | 53.49%
2022-01-08 | 44569 |  | 51.42%
2022-01-08 01:00 | 44569.0417 |  | 50.91%
2022-01-08 02:00 | 44569.0833 |  | 50.8%
2022-01-08 03:00 | 44569.125 |  | 50.66%
2022-01-08 04:00 | 44569.1667 |  | 50.6%
2022-01-08 05:00 | 44569.2083 |  | 50.46%
2022-01-08 06:00 | 44569.25 |  | 50.89%
2022-01-08 07:00 | 44569.2917 |  | 51.57%
2022-01-08 08:00 | 44569.3333 |  | 52.79%
2022-01-08 09:00 | 44569.375 |  | 53.66%
2022-01-08 10:00 | 44569.4167 |  | 54.4%
2022-01-08 11:00 | 44569.4583 |  | 54.63%
2022-01-08 12:00 | 44569.5 |  | 54.65%
2022-01-08 13:00 | 44569.5417 |  | 54.18%
2022-01-08 14:00 | 44569.5833 |  | 54.16%
2022-01-08 15:00 | 44569.625 |  | 54.14%
2022-01-08 16:00 | 44569.6667 |  | 54.04%
2022-01-08 17:00 | 44569.7083 |  | 53.9%
2022-01-08 18:00 | 44569.75 |  | 53.38%
2022-01-08 19:00 | 44569.7917 |  | 52.67%
2022-01-08 20:00 | 44569.8333 |  | 52.05%
2022-01-08 21:00 | 44569.875 |  | 52.27%
2022-01-08 22:00 | 44569.9167 |  | 52.14%
2022-01-08 23:00 | 44569.9583 |  | 52.47%
2022-01-09 | 44570 |  | 51.92%
2022-01-09 01:00 | 44570.0417 |  | 51.4%
2022-01-09 02:00 | 44570.0833 |  | 51.29%
2022-01-09 03:00 | 44570.125 |  | 51.15%
2022-01-09 04:00 | 44570.1667 |  | 51.09%
2022-01-09 05:00 | 44570.2083 |  | 50.95%
2022-01-09 06:00 | 44570.25 |  | 51.38%
2022-01-09 07:00 | 44570.2917 |  | 52.07%
2022-01-09 08:00 | 44570.3333 |  | 53.29%
2022-01-09 09:00 | 44570.375 |  | 54.17%
2022-01-09 10:00 | 44570.4167 |  | 54.93%
2022-01-09 11:00 | 44570.4583 |  | 55.16%
2022-01-09 12:00 | 44570.5 |  | 55.18%
2022-01-09 13:00 | 44570.5417 |  | 54.7%
2022-01-09 14:00 | 44570.5833 |  | 54.68%
2022-01-09 15:00 | 44570.625 |  | 54.66%
2022-01-09 16:00 | 44570.6667 |  | 54.56%
2022-01-09 17:00 | 44570.7083 |  | 54.42%
2022-01-09 18:00 | 44570.75 |  | 53.89%
2022-01-09 19:00 | 44570.7917 |  | 53.18%
2022-01-09 20:00 | 44570.8333 |  | 52.55%
2022-01-09 21:00 | 44570.875 |  | 52.78%
2022-01-09 22:00 | 44570.9167 |  | 52.65%
2022-01-09 23:00 | 44570.9583 |  | 52.97%
2022-01-10 | 44571 |  | 52.63%
2022-01-10 01:00 | 44571.0417 |  | 51.97%
2022-01-10 02:00 | 44571.0833 |  | 51.59%
2022-01-10 03:00 | 44571.125 |  | 51.39%
2022-01-10 04:00 | 44571.1667 |  | 51.12%
2022-01-10 05:00 | 44571.2083 |  | 50.95%
2022-01-10 06:00 | 44571.25 |  | 52.22%
2022-01-10 07:00 | 44571.2917 |  | 54.28%
2022-01-10 08:00 | 44571.3333 |  | 54.87%
2022-01-10 09:00 | 44571.375 |  | 54.07%
2022-01-10 10:00 | 44571.4167 |  | 53.59%
2022-01-10 11:00 | 44571.4583 |  | 53.94%
2022-01-10 12:00 | 44571.5 |  | 53.89%
2022-01-10 13:00 | 44571.5417 |  | 53.81%
2022-01-10 14:00 | 44571.5833 |  | 54.28%
2022-01-10 15:00 | 44571.625 |  | 54.67%
2022-01-10 16:00 | 44571.6667 |  | 54.67%
2022-01-10 17:00 | 44571.7083 |  | 54.5%
2022-01-10 18:00 | 44571.75 |  | 54.25%
2022-01-10 19:00 | 44571.7917 |  | 53.86%
2022-01-10 20:00 | 44571.8333 |  | 53.25%
2022-01-10 21:00 | 44571.875 |  | 53.34%
2022-01-10 22:00 | 44571.9167 |  | 52.99%
2022-01-10 23:00 | 44571.9583 |  | 53.38%
2022-01-11 | 44572 |  | 52.34%
2022-01-11 01:00 | 44572.0417 |  | 51.68%
2022-01-11 02:00 | 44572.0833 |  | 51.3%
2022-01-11 03:00 | 44572.125 |  | 51.11%
2022-01-11 04:00 | 44572.1667 |  | 50.83%
2022-01-11 05:00 | 44572.2083 |  | 50.66%
2022-01-11 06:00 | 44572.25 |  | 51.93%
2022-01-11 07:00 | 44572.2917 |  | 53.98%
2022-01-11 08:00 | 44572.3333 |  | 54.56%
2022-01-11 09:00 | 44572.375 |  | 53.77%
2022-01-11 10:00 | 44572.4167 |  | 53.29%
2022-01-11 11:00 | 44572.4583 |  | 53.64%
2022-01-11 12:00 | 44572.5 |  | 53.59%
2022-01-11 13:00 | 44572.5417 |  | 53.51%
2022-01-11 14:00 | 44572.5833 |  | 53.98%
2022-01-11 15:00 | 44572.625 |  | 54.37%
2022-01-11 16:00 | 44572.6667 |  | 54.36%
2022-01-11 17:00 | 44572.7083 |  | 54.2%
2022-01-11 18:00 | 44572.75 |  | 53.95%
2022-01-11 19:00 | 44572.7917 |  | 53.56%
2022-01-11 20:00 | 44572.8333 |  | 52.95%
2022-01-11 21:00 | 44572.875 |  | 53.04%
2022-01-11 22:00 | 44572.9167 |  | 52.69%
2022-01-11 23:00 | 44572.9583 |  | 53.08%
2022-01-12 | 44573 |  | 52.25%
2022-01-12 01:00 | 44573.0417 |  | 51.58%
2022-01-12 02:00 | 44573.0833 |  | 51.2%
2022-01-12 03:00 | 44573.125 |  | 51.01%
2022-01-12 04:00 | 44573.1667 |  | 50.74%
2022-01-12 05:00 | 44573.2083 |  | 50.57%
2022-01-12 06:00 | 44573.25 |  | 51.83%
2022-01-12 07:00 | 44573.2917 |  | 53.88%
2022-01-12 08:00 | 44573.3333 |  | 54.46%
2022-01-12 09:00 | 44573.375 |  | 53.68%
2022-01-12 10:00 | 44573.4167 |  | 53.2%
2022-01-12 11:00 | 44573.4583 |  | 53.54%
2022-01-12 12:00 | 44573.5 |  | 53.49%
2022-01-12 13:00 | 44573.5417 |  | 53.41%
2022-01-12 14:00 | 44573.5833 |  | 53.88%
2022-01-12 15:00 | 44573.625 |  | 54.27%
2022-01-12 16:00 | 44573.6667 |  | 54.26%
2022-01-12 17:00 | 44573.7083 |  | 54.1%
2022-01-12 18:00 | 44573.75 |  | 53.85%
2022-01-12 19:00 | 44573.7917 |  | 53.47%
2022-01-12 20:00 | 44573.8333 |  | 52.85%
2022-01-12 21:00 | 44573.875 |  | 52.94%
2022-01-12 22:00 | 44573.9167 |  | 52.59%
2022-01-12 23:00 | 44573.9583 |  | 52.98%
2022-01-13 | 44574 |  | 52.29%
2022-01-13 01:00 | 44574.0417 |  | 51.62%
2022-01-13 02:00 | 44574.0833 |  | 51.24%
2022-01-13 03:00 | 44574.125 |  | 51.05%
2022-01-13 04:00 | 44574.1667 |  | 50.78%
2022-01-13 05:00 | 44574.2083 |  | 50.61%
2022-01-13 06:00 | 44574.25 |  | 51.87%
2022-01-13 07:00 | 44574.2917 |  | 53.92%
2022-01-13 08:00 | 44574.3333 |  | 54.5%
2022-01-13 09:00 | 44574.375 |  | 53.72%
2022-01-13 10:00 | 44574.4167 |  | 53.24%
2022-01-13 11:00 | 44574.4583 |  | 53.58%
2022-01-13 12:00 | 44574.5 |  | 53.53%
2022-01-13 13:00 | 44574.5417 |  | 53.45%
2022-01-13 14:00 | 44574.5833 |  | 53.92%
2022-01-13 15:00 | 44574.625 |  | 54.31%
2022-01-13 16:00 | 44574.6667 |  | 54.3%
2022-01-13 17:00 | 44574.7083 |  | 54.14%
2022-01-13 18:00 | 44574.75 |  | 53.89%
2022-01-13 19:00 | 44574.7917 |  | 53.51%
2022-01-13 20:00 | 44574.8333 |  | 52.89%
2022-01-13 21:00 | 44574.875 |  | 52.98%
2022-01-13 22:00 | 44574.9167 |  | 52.63%
2022-01-13 23:00 | 44574.9583 |  | 53.02%
2022-01-14 | 44575 |  | 51.7%
2022-01-14 01:00 | 44575.0417 |  | 51.04%
2022-01-14 02:00 | 44575.0833 |  | 50.67%
2022-01-14 03:00 | 44575.125 |  | 50.48%
2022-01-14 04:00 | 44575.1667 |  | 50.21%
2022-01-14 05:00 | 44575.2083 |  | 50.04%
2022-01-14 06:00 | 44575.25 |  | 51.29%
2022-01-14 07:00 | 44575.2917 |  | 53.32%
2022-01-14 08:00 | 44575.3333 |  | 53.9%
2022-01-14 09:00 | 44575.375 |  | 53.12%
2022-01-14 10:00 | 44575.4167 |  | 52.64%
2022-01-14 11:00 | 44575.4583 |  | 52.98%
2022-01-14 12:00 | 44575.5 |  | 52.93%
2022-01-14 13:00 | 44575.5417 |  | 52.85%
2022-01-14 14:00 | 44575.5833 |  | 53.32%
2022-01-14 15:00 | 44575.625 |  | 53.7%
2022-01-14 16:00 | 44575.6667 |  | 53.7%
2022-01-14 17:00 | 44575.7083 |  | 53.53%
2022-01-14 18:00 | 44575.75 |  | 53.29%
2022-01-14 19:00 | 44575.7917 |  | 52.91%
2022-01-14 20:00 | 44575.8333 |  | 52.3%
2022-01-14 21:00 | 44575.875 |  | 52.39%
2022-01-14 22:00 | 44575.9167 |  | 52.05%
2022-01-14 23:00 | 44575.9583 |  | 52.43%
2022-01-15 | 44576 |  | 51%
2022-01-15 01:00 | 44576.0417 |  | 50.5%
2022-01-15 02:00 | 44576.0833 |  | 50.39%
2022-01-15 03:00 | 44576.125 |  | 50.25%
2022-01-15 04:00 | 44576.1667 |  | 50.19%
2022-01-15 05:00 | 44576.2083 |  | 50.05%
2022-01-15 06:00 | 44576.25 |  | 50.47%
2022-01-15 07:00 | 44576.2917 |  | 51.16%
2022-01-15 08:00 | 44576.3333 |  | 52.36%
2022-01-15 09:00 | 44576.375 |  | 53.22%
2022-01-15 10:00 | 44576.4167 |  | 53.96%
2022-01-15 11:00 | 44576.4583 |  | 54.19%
2022-01-15 12:00 | 44576.5 |  | 54.21%
2022-01-15 13:00 | 44576.5417 |  | 53.74%
2022-01-15 14:00 | 44576.5833 |  | 53.72%
2022-01-15 15:00 | 44576.625 |  | 53.7%
2022-01-15 16:00 | 44576.6667 |  | 53.6%
2022-01-15 17:00 | 44576.7083 |  | 53.47%
2022-01-15 18:00 | 44576.75 |  | 52.95%
2022-01-15 19:00 | 44576.7917 |  | 52.24%
2022-01-15 20:00 | 44576.8333 |  | 51.62%
2022-01-15 21:00 | 44576.875 |  | 51.85%
2022-01-15 22:00 | 44576.9167 |  | 51.72%
2022-01-15 23:00 | 44576.9583 |  | 52.04%
2022-01-16 | 44577 |  | 51.19%
2022-01-16 01:00 | 44577.0417 |  | 50.68%
2022-01-16 02:00 | 44577.0833 |  | 50.58%
2022-01-16 03:00 | 44577.125 |  | 50.43%
2022-01-16 04:00 | 44577.1667 |  | 50.37%
2022-01-16 05:00 | 44577.2083 |  | 50.24%
2022-01-16 06:00 | 44577.25 |  | 50.66%
2022-01-16 07:00 | 44577.2917 |  | 51.34%
2022-01-16 08:00 | 44577.3333 |  | 52.55%
2022-01-16 09:00 | 44577.375 |  | 53.42%
2022-01-16 10:00 | 44577.4167 |  | 54.16%
2022-01-16 11:00 | 44577.4583 |  | 54.38%
2022-01-16 12:00 | 44577.5 |  | 54.41%
2022-01-16 13:00 | 44577.5417 |  | 53.94%
2022-01-16 14:00 | 44577.5833 |  | 53.91%
2022-01-16 15:00 | 44577.625 |  | 53.89%
2022-01-16 16:00 | 44577.6667 |  | 53.79%
2022-01-16 17:00 | 44577.7083 |  | 53.66%
2022-01-16 18:00 | 44577.75 |  | 53.14%
2022-01-16 19:00 | 44577.7917 |  | 52.43%
2022-01-16 20:00 | 44577.8333 |  | 51.81%
2022-01-16 21:00 | 44577.875 |  | 52.04%
2022-01-16 22:00 | 44577.9167 |  | 51.91%
2022-01-16 23:00 | 44577.9583 |  | 52.23%
2022-01-17 | 44578 |  | 51.96%
2022-01-17 01:00 | 44578.0417 |  | 51.3%
2022-01-17 02:00 | 44578.0833 |  | 50.93%
2022-01-17 03:00 | 44578.125 |  | 50.73%
2022-01-17 04:00 | 44578.1667 |  | 50.46%
2022-01-17 05:00 | 44578.2083 |  | 50.29%
2022-01-17 06:00 | 44578.25 |  | 51.55%
2022-01-17 07:00 | 44578.2917 |  | 53.58%
2022-01-17 08:00 | 44578.3333 |  | 54.17%
2022-01-17 09:00 | 44578.375 |  | 53.38%
2022-01-17 10:00 | 44578.4167 |  | 52.91%
2022-01-17 11:00 | 44578.4583 |  | 53.25%
2022-01-17 12:00 | 44578.5 |  | 53.2%
2022-01-17 13:00 | 44578.5417 |  | 53.12%
2022-01-17 14:00 | 44578.5833 |  | 53.59%
2022-01-17 15:00 | 44578.625 |  | 53.97%
2022-01-17 16:00 | 44578.6667 |  | 53.97%
2022-01-17 17:00 | 44578.7083 |  | 53.8%
2022-01-17 18:00 | 44578.75 |  | 53.56%
2022-01-17 19:00 | 44578.7917 |  | 53.18%
2022-01-17 20:00 | 44578.8333 |  | 52.56%
2022-01-17 21:00 | 44578.875 |  | 52.65%
2022-01-17 22:00 | 44578.9167 |  | 52.31%
2022-01-17 23:00 | 44578.9583 |  | 52.69%
2022-01-18 | 44579 |  | 52.63%
2022-01-18 01:00 | 44579.0417 |  | 51.96%
2022-01-18 02:00 | 44579.0833 |  | 51.58%
2022-01-18 03:00 | 44579.125 |  | 51.39%
2022-01-18 04:00 | 44579.1667 |  | 51.12%
2022-01-18 05:00 | 44579.2083 |  | 50.94%
2022-01-18 06:00 | 44579.25 |  | 52.22%
2022-01-18 07:00 | 44579.2917 |  | 54.28%
2022-01-18 08:00 | 44579.3333 |  | 54.87%
2022-01-18 09:00 | 44579.375 |  | 54.07%
2022-01-18 10:00 | 44579.4167 |  | 53.59%
2022-01-18 11:00 | 44579.4583 |  | 53.94%
2022-01-18 12:00 | 44579.5 |  | 53.89%
2022-01-18 13:00 | 44579.5417 |  | 53.81%
2022-01-18 14:00 | 44579.5833 |  | 54.28%
2022-01-18 15:00 | 44579.625 |  | 54.67%
2022-01-18 16:00 | 44579.6667 |  | 54.67%
2022-01-18 17:00 | 44579.7083 |  | 54.5%
2022-01-18 18:00 | 44579.75 |  | 54.25%
2022-01-18 19:00 | 44579.7917 |  | 53.86%
2022-01-18 20:00 | 44579.8333 |  | 53.25%
2022-01-18 21:00 | 44579.875 |  | 53.33%
2022-01-18 22:00 | 44579.9167 |  | 52.99%
2022-01-18 23:00 | 44579.9583 |  | 53.38%
2022-01-19 | 44580 |  | 53.02%
2022-01-19 01:00 | 44580.0417 |  | 52.35%
2022-01-19 02:00 | 44580.0833 |  | 51.96%
2022-01-19 03:00 | 44580.125 |  | 51.77%
2022-01-19 04:00 | 44580.1667 |  | 51.49%
2022-01-19 05:00 | 44580.2083 |  | 51.32%
2022-01-19 06:00 | 44580.25 |  | 52.6%
2022-01-19 07:00 | 44580.2917 |  | 54.68%
2022-01-19 08:00 | 44580.3333 |  | 55.27%
2022-01-19 09:00 | 44580.375 |  | 54.47%
2022-01-19 10:00 | 44580.4167 |  | 53.98%
2022-01-19 11:00 | 44580.4583 |  | 54.33%
2022-01-19 12:00 | 44580.5 |  | 54.28%
2022-01-19 13:00 | 44580.5417 |  | 54.2%
2022-01-19 14:00 | 44580.5833 |  | 54.68%
2022-01-19 15:00 | 44580.625 |  | 55.07%
2022-01-19 16:00 | 44580.6667 |  | 55.07%
2022-01-19 17:00 | 44580.7083 |  | 54.9%
2022-01-19 18:00 | 44580.75 |  | 54.65%
2022-01-19 19:00 | 44580.7917 |  | 54.26%
2022-01-19 20:00 | 44580.8333 |  | 53.64%
2022-01-19 21:00 | 44580.875 |  | 53.73%
2022-01-19 22:00 | 44580.9167 |  | 53.37%
2022-01-19 23:00 | 44580.9583 |  | 53.77%
2022-01-20 | 44581 |  | 53.11%
2022-01-20 01:00 | 44581.0417 |  | 52.43%
2022-01-20 02:00 | 44581.0833 |  | 52.05%
2022-01-20 03:00 | 44581.125 |  | 51.85%
2022-01-20 04:00 | 44581.1667 |  | 51.58%
2022-01-20 05:00 | 44581.2083 |  | 51.4%
2022-01-20 06:00 | 44581.25 |  | 52.69%
2022-01-20 07:00 | 44581.2917 |  | 54.77%
2022-01-20 08:00 | 44581.3333 |  | 55.36%
2022-01-20 09:00 | 44581.375 |  | 54.56%
2022-01-20 10:00 | 44581.4167 |  | 54.07%
2022-01-20 11:00 | 44581.4583 |  | 54.42%
2022-01-20 12:00 | 44581.5 |  | 54.37%
2022-01-20 13:00 | 44581.5417 |  | 54.29%
2022-01-20 14:00 | 44581.5833 |  | 54.77%
2022-01-20 15:00 | 44581.625 |  | 55.16%
2022-01-20 16:00 | 44581.6667 |  | 55.16%
2022-01-20 17:00 | 44581.7083 |  | 54.99%
2022-01-20 18:00 | 44581.75 |  | 54.74%
2022-01-20 19:00 | 44581.7917 |  | 54.35%
2022-01-20 20:00 | 44581.8333 |  | 53.72%
2022-01-20 21:00 | 44581.875 |  | 53.81%
2022-01-20 22:00 | 44581.9167 |  | 53.46%
2022-01-20 23:00 | 44581.9583 |  | 53.86%
2022-01-21 | 44582 |  | 53.01%
2022-01-21 01:00 | 44582.0417 |  | 52.34%
2022-01-21 02:00 | 44582.0833 |  | 51.95%
2022-01-21 03:00 | 44582.125 |  | 51.76%
2022-01-21 04:00 | 44582.1667 |  | 51.48%
2022-01-21 05:00 | 44582.2083 |  | 51.31%
2022-01-21 06:00 | 44582.25 |  | 52.59%
2022-01-21 07:00 | 44582.2917 |  | 54.67%
2022-01-21 08:00 | 44582.3333 |  | 55.26%
2022-01-21 09:00 | 44582.375 |  | 54.46%
2022-01-21 10:00 | 44582.4167 |  | 53.98%
2022-01-21 11:00 | 44582.4583 |  | 54.32%
2022-01-21 12:00 | 44582.5 |  | 54.27%
2022-01-21 13:00 | 44582.5417 |  | 54.19%
2022-01-21 14:00 | 44582.5833 |  | 54.67%
2022-01-21 15:00 | 44582.625 |  | 55.06%
2022-01-21 16:00 | 44582.6667 |  | 55.06%
2022-01-21 17:00 | 44582.7083 |  | 54.89%
2022-01-21 18:00 | 44582.75 |  | 54.64%
2022-01-21 19:00 | 44582.7917 |  | 54.25%
2022-01-21 20:00 | 44582.8333 |  | 53.63%
2022-01-21 21:00 | 44582.875 |  | 53.72%
2022-01-21 22:00 | 44582.9167 |  | 53.37%
2022-01-21 23:00 | 44582.9583 |  | 53.76%
2022-01-22 | 44583 |  | 52.37%
2022-01-22 01:00 | 44583.0417 |  | 51.85%
2022-01-22 02:00 | 44583.0833 |  | 51.75%
2022-01-22 03:00 | 44583.125 |  | 51.6%
2022-01-22 04:00 | 44583.1667 |  | 51.54%
2022-01-22 05:00 | 44583.2083 |  | 51.4%
2022-01-22 06:00 | 44583.25 |  | 51.83%
2022-01-22 07:00 | 44583.2917 |  | 52.53%
2022-01-22 08:00 | 44583.3333 |  | 53.76%
2022-01-22 09:00 | 44583.375 |  | 54.65%
2022-01-22 10:00 | 44583.4167 |  | 55.41%
2022-01-22 11:00 | 44583.4583 |  | 55.64%
2022-01-22 12:00 | 44583.5 |  | 55.67%
2022-01-22 13:00 | 44583.5417 |  | 55.18%
2022-01-22 14:00 | 44583.5833 |  | 55.16%
2022-01-22 15:00 | 44583.625 |  | 55.14%
2022-01-22 16:00 | 44583.6667 |  | 55.04%
2022-01-22 17:00 | 44583.7083 |  | 54.9%
2022-01-22 18:00 | 44583.75 |  | 54.37%
2022-01-22 19:00 | 44583.7917 |  | 53.65%
2022-01-22 20:00 | 44583.8333 |  | 53.01%
2022-01-22 21:00 | 44583.875 |  | 53.24%
2022-01-22 22:00 | 44583.9167 |  | 53.11%
2022-01-22 23:00 | 44583.9583 |  | 53.44%
2022-01-23 | 44584 |  | 51.71%
2022-01-23 01:00 | 44584.0417 |  | 51.2%
2022-01-23 02:00 | 44584.0833 |  | 51.09%
2022-01-23 03:00 | 44584.125 |  | 50.95%
2022-01-23 04:00 | 44584.1667 |  | 50.89%
2022-01-23 05:00 | 44584.2083 |  | 50.75%
2022-01-23 06:00 | 44584.25 |  | 51.18%
2022-01-23 07:00 | 44584.2917 |  | 51.87%
2022-01-23 08:00 | 44584.3333 |  | 53.09%
2022-01-23 09:00 | 44584.375 |  | 53.96%
2022-01-23 10:00 | 44584.4167 |  | 54.71%
2022-01-23 11:00 | 44584.4583 |  | 54.94%
2022-01-23 12:00 | 44584.5 |  | 54.96%
2022-01-23 13:00 | 44584.5417 |  | 54.49%
2022-01-23 14:00 | 44584.5833 |  | 54.47%
2022-01-23 15:00 | 44584.625 |  | 54.45%
2022-01-23 16:00 | 44584.6667 |  | 54.34%
2022-01-23 17:00 | 44584.7083 |  | 54.21%
2022-01-23 18:00 | 44584.75 |  | 53.69%
2022-01-23 19:00 | 44584.7917 |  | 52.97%
2022-01-23 20:00 | 44584.8333 |  | 52.34%
2022-01-23 21:00 | 44584.875 |  | 52.57%
2022-01-23 22:00 | 44584.9167 |  | 52.44%
2022-01-23 23:00 | 44584.9583 |  | 52.77%
2022-01-24 | 44585 |  | 52.31%
2022-01-24 01:00 | 44585.0417 |  | 51.65%
2022-01-24 02:00 | 44585.0833 |  | 51.27%
2022-01-24 03:00 | 44585.125 |  | 51.08%
2022-01-24 04:00 | 44585.1667 |  | 50.8%
2022-01-24 05:00 | 44585.2083 |  | 50.64%
2022-01-24 06:00 | 44585.25 |  | 51.9%
2022-01-24 07:00 | 44585.2917 |  | 53.95%
2022-01-24 08:00 | 44585.3333 |  | 54.53%
2022-01-24 09:00 | 44585.375 |  | 53.75%
2022-01-24 10:00 | 44585.4167 |  | 53.27%
2022-01-24 11:00 | 44585.4583 |  | 53.61%
2022-01-24 12:00 | 44585.5 |  | 53.56%
2022-01-24 13:00 | 44585.5417 |  | 53.48%
2022-01-24 14:00 | 44585.5833 |  | 53.95%
2022-01-24 15:00 | 44585.625 |  | 54.34%
2022-01-24 16:00 | 44585.6667 |  | 54.34%
2022-01-24 17:00 | 44585.7083 |  | 54.17%
2022-01-24 18:00 | 44585.75 |  | 53.92%
2022-01-24 19:00 | 44585.7917 |  | 53.54%
2022-01-24 20:00 | 44585.8333 |  | 52.92%
2022-01-24 21:00 | 44585.875 |  | 53.01%
2022-01-24 22:00 | 44585.9167 |  | 52.66%
2022-01-24 23:00 | 44585.9583 |  | 53.05%
2022-01-25 | 44586 |  | 52.78%
2022-01-25 01:00 | 44586.0417 |  | 52.11%
2022-01-25 02:00 | 44586.0833 |  | 51.73%
2022-01-25 03:00 | 44586.125 |  | 51.54%
2022-01-25 04:00 | 44586.1667 |  | 51.26%
2022-01-25 05:00 | 44586.2083 |  | 51.09%
2022-01-25 06:00 | 44586.25 |  | 52.37%
2022-01-25 07:00 | 44586.2917 |  | 54.43%
2022-01-25 08:00 | 44586.3333 |  | 55.02%
2022-01-25 09:00 | 44586.375 |  | 54.23%
2022-01-25 10:00 | 44586.4167 |  | 53.74%
2022-01-25 11:00 | 44586.4583 |  | 54.09%
2022-01-25 12:00 | 44586.5 |  | 54.04%
2022-01-25 13:00 | 44586.5417 |  | 53.96%
2022-01-25 14:00 | 44586.5833 |  | 54.43%
2022-01-25 15:00 | 44586.625 |  | 54.82%
2022-01-25 16:00 | 44586.6667 |  | 54.82%
2022-01-25 17:00 | 44586.7083 |  | 54.65%
2022-01-25 18:00 | 44586.75 |  | 54.41%
2022-01-25 19:00 | 44586.7917 |  | 54.02%
2022-01-25 20:00 | 44586.8333 |  | 53.4%
2022-01-25 21:00 | 44586.875 |  | 53.49%
2022-01-25 22:00 | 44586.9167 |  | 53.14%
2022-01-25 23:00 | 44586.9583 |  | 53.53%
2022-01-26 | 44587 |  | 53.01%
2022-01-26 01:00 | 44587.0417 |  | 52.33%
2022-01-26 02:00 | 44587.0833 |  | 51.95%
2022-01-26 03:00 | 44587.125 |  | 51.75%
2022-01-26 04:00 | 44587.1667 |  | 51.48%
2022-01-26 05:00 | 44587.2083 |  | 51.3%
2022-01-26 06:00 | 44587.25 |  | 52.59%
2022-01-26 07:00 | 44587.2917 |  | 54.66%
2022-01-26 08:00 | 44587.3333 |  | 55.25%
2022-01-26 09:00 | 44587.375 |  | 54.46%
2022-01-26 10:00 | 44587.4167 |  | 53.97%
2022-01-26 11:00 | 44587.4583 |  | 54.32%
2022-01-26 12:00 | 44587.5 |  | 54.27%
2022-01-26 13:00 | 44587.5417 |  | 54.19%
2022-01-26 14:00 | 44587.5833 |  | 54.66%
2022-01-26 15:00 | 44587.625 |  | 55.06%
2022-01-26 16:00 | 44587.6667 |  | 55.05%
2022-01-26 17:00 | 44587.7083 |  | 54.88%
2022-01-26 18:00 | 44587.75 |  | 54.64%
2022-01-26 19:00 | 44587.7917 |  | 54.24%
2022-01-26 20:00 | 44587.8333 |  | 53.62%
2022-01-26 21:00 | 44587.875 |  | 53.71%
2022-01-26 22:00 | 44587.9167 |  | 53.36%
2022-01-26 23:00 | 44587.9583 |  | 53.75%
2022-01-27 | 44588 |  | 51.61%
2022-01-27 01:00 | 44588.0417 |  | 50.89%
2022-01-27 02:00 | 44588.0833 |  | 50.39%
2022-01-27 03:00 | 44588.125 |  | 50.42%
2022-01-27 04:00 | 44588.1667 |  | 50.06%
2022-01-27 05:00 | 44588.2083 |  | 50.49%
2022-01-27 06:00 | 44588.25 |  | 53.53%
2022-01-27 07:00 | 44588.2917 |  | 57.29%
2022-01-27 08:00 | 44588.3333 |  | 58.06%
2022-01-27 09:00 | 44588.375 |  | 57.24%
2022-01-27 10:00 | 44588.4167 |  | 57.17%
2022-01-27 11:00 | 44588.4583 |  | 57.48%
2022-01-27 12:00 | 44588.5 |  | 57.53%
2022-01-27 13:00 | 44588.5417 |  | 57.63%
2022-01-27 14:00 | 44588.5833 |  | 57.91%
2022-01-27 15:00 | 44588.625 |  | 58.02%
2022-01-27 16:00 | 44588.6667 |  | 57.99%
2022-01-27 17:00 | 44588.7083 |  | 57.68%
2022-01-27 18:00 | 44588.75 |  | 56.63%
2022-01-27 19:00 | 44588.7917 |  | 56.51%
2022-01-27 20:00 | 44588.8333 |  | 54.76%
2022-01-27 21:00 | 44588.875 |  | 54.56%
2022-01-27 22:00 | 44588.9167 |  | 53.54%
2022-01-27 23:00 | 44588.9583 |  | 54.08%
2022-01-28 | 44589 |  | 51.59%
2022-01-28 01:00 | 44589.0417 |  | 50.87%
2022-01-28 02:00 | 44589.0833 |  | 50.37%
2022-01-28 03:00 | 44589.125 |  | 50.41%
2022-01-28 04:00 | 44589.1667 |  | 50.05%
2022-01-28 05:00 | 44589.2083 |  | 50.48%
2022-01-28 06:00 | 44589.25 |  | 53.51%
2022-01-28 07:00 | 44589.2917 |  | 57.28%
2022-01-28 08:00 | 44589.3333 |  | 58.05%
2022-01-28 09:00 | 44589.375 |  | 57.22%
2022-01-28 10:00 | 44589.4167 |  | 57.16%
2022-01-28 11:00 | 44589.4583 |  | 57.46%
2022-01-28 12:00 | 44589.5 |  | 57.52%
2022-01-28 13:00 | 44589.5417 |  | 57.62%
2022-01-28 14:00 | 44589.5833 |  | 57.89%
2022-01-28 15:00 | 44589.625 |  | 58%
2022-01-28 16:00 | 44589.6667 |  | 57.98%
2022-01-28 17:00 | 44589.7083 |  | 57.66%
2022-01-28 18:00 | 44589.75 |  | 56.61%
2022-01-28 19:00 | 44589.7917 |  | 56.5%
2022-01-28 20:00 | 44589.8333 |  | 54.74%
2022-01-28 21:00 | 44589.875 |  | 54.54%
2022-01-28 22:00 | 44589.9167 |  | 53.52%
2022-01-28 23:00 | 44589.9583 |  | 54.06%
2022-01-29 | 44590 |  | 50.29%
2022-01-29 01:00 | 44590.0417 |  | 49.99%
2022-01-29 02:00 | 44590.0833 |  | 49.54%
2022-01-29 03:00 | 44590.125 |  | 49.17%
2022-01-29 04:00 | 44590.1667 |  | 48.92%
2022-01-29 05:00 | 44590.2083 |  | 49.19%
2022-01-29 06:00 | 44590.25 |  | 49.86%
2022-01-29 07:00 | 44590.2917 |  | 51.77%
2022-01-29 08:00 | 44590.3333 |  | 54.04%
2022-01-29 09:00 | 44590.375 |  | 55.51%
2022-01-29 10:00 | 44590.4167 |  | 56.06%
2022-01-29 11:00 | 44590.4583 |  | 56.59%
2022-01-29 12:00 | 44590.5 |  | 56.64%
2022-01-29 13:00 | 44590.5417 |  | 56.53%
2022-01-29 14:00 | 44590.5833 |  | 55.87%
2022-01-29 15:00 | 44590.625 |  | 55.41%
2022-01-29 16:00 | 44590.6667 |  | 54.82%
2022-01-29 17:00 | 44590.7083 |  | 54.76%
2022-01-29 18:00 | 44590.75 |  | 53.55%
2022-01-29 19:00 | 44590.7917 |  | 53.39%
2022-01-29 20:00 | 44590.8333 |  | 51.64%
2022-01-29 21:00 | 44590.875 |  | 50.61%
2022-01-29 22:00 | 44590.9167 |  | 49.84%
2022-01-29 23:00 | 44590.9583 |  | 50.39%
2022-01-30 | 44591 |  | 49.74%
2022-01-30 01:00 | 44591.0417 |  | 49.44%
2022-01-30 02:00 | 44591.0833 |  | 48.99%
2022-01-30 03:00 | 44591.125 |  | 48.63%
2022-01-30 04:00 | 44591.1667 |  | 48.38%
2022-01-30 05:00 | 44591.2083 |  | 48.64%
2022-01-30 06:00 | 44591.25 |  | 49.31%
2022-01-30 07:00 | 44591.2917 |  | 51.2%
2022-01-30 08:00 | 44591.3333 |  | 53.44%
2022-01-30 09:00 | 44591.375 |  | 54.89%
2022-01-30 10:00 | 44591.4167 |  | 55.43%
2022-01-30 11:00 | 44591.4583 |  | 55.96%
2022-01-30 12:00 | 44591.5 |  | 56.01%
2022-01-30 13:00 | 44591.5417 |  | 55.9%
2022-01-30 14:00 | 44591.5833 |  | 55.25%
2022-01-30 15:00 | 44591.625 |  | 54.79%
2022-01-30 16:00 | 44591.6667 |  | 54.21%
2022-01-30 17:00 | 44591.7083 |  | 54.15%
2022-01-30 18:00 | 44591.75 |  | 52.96%
2022-01-30 19:00 | 44591.7917 |  | 52.8%
2022-01-30 20:00 | 44591.8333 |  | 51.07%
2022-01-30 21:00 | 44591.875 |  | 50.05%
2022-01-30 22:00 | 44591.9167 |  | 49.28%
2022-01-30 23:00 | 44591.9583 |  | 49.83%
2022-01-31 | 44592 |  | 50.17%
2022-01-31 01:00 | 44592.0417 |  | 49.47%
2022-01-31 02:00 | 44592.0833 |  | 48.98%
2022-01-31 03:00 | 44592.125 |  | 49.02%
2022-01-31 04:00 | 44592.1667 |  | 48.67%
2022-01-31 05:00 | 44592.2083 |  | 49.09%
2022-01-31 06:00 | 44592.25 |  | 52.04%
2022-01-31 07:00 | 44592.2917 |  | 55.7%
2022-01-31 08:00 | 44592.3333 |  | 56.45%
2022-01-31 09:00 | 44592.375 |  | 55.64%
2022-01-31 10:00 | 44592.4167 |  | 55.58%
2022-01-31 11:00 | 44592.4583 |  | 55.87%
2022-01-31 12:00 | 44592.5 |  | 55.93%
2022-01-31 13:00 | 44592.5417 |  | 56.03%
2022-01-31 14:00 | 44592.5833 |  | 56.29%
2022-01-31 15:00 | 44592.625 |  | 56.4%
2022-01-31 16:00 | 44592.6667 |  | 56.38%
2022-01-31 17:00 | 44592.7083 |  | 56.07%
2022-01-31 18:00 | 44592.75 |  | 55.05%
2022-01-31 19:00 | 44592.7917 |  | 54.94%
2022-01-31 20:00 | 44592.8333 |  | 53.23%
2022-01-31 21:00 | 44592.875 |  | 53.04%
2022-01-31 22:00 | 44592.9167 |  | 52.05%
2022-01-31 23:00 | 44592.9583 |  | 52.57%
2022-02-01 | 44593 |  | 50.08%
2022-02-01 01:00 | 44593.0417 |  | 49.39%
2022-02-01 02:00 | 44593.0833 |  | 48.9%
2022-02-01 03:00 | 44593.125 |  | 48.93%
2022-02-01 04:00 | 44593.1667 |  | 48.59%
2022-02-01 05:00 | 44593.2083 |  | 49%
2022-02-01 06:00 | 44593.25 |  | 51.95%
2022-02-01 07:00 | 44593.2917 |  | 55.6%
2022-02-01 08:00 | 44593.3333 |  | 56.35%
2022-02-01 09:00 | 44593.375 |  | 55.55%
2022-02-01 10:00 | 44593.4167 |  | 55.49%
2022-02-01 11:00 | 44593.4583 |  | 55.78%
2022-02-01 12:00 | 44593.5 |  | 55.84%
2022-02-01 13:00 | 44593.5417 |  | 55.93%
2022-02-01 14:00 | 44593.5833 |  | 56.2%
2022-02-01 15:00 | 44593.625 |  | 56.3%
2022-02-01 16:00 | 44593.6667 |  | 56.28%
2022-02-01 17:00 | 44593.7083 |  | 55.97%
2022-02-01 18:00 | 44593.75 |  | 54.95%
2022-02-01 19:00 | 44593.7917 |  | 54.85%
2022-02-01 20:00 | 44593.8333 |  | 53.14%
2022-02-01 21:00 | 44593.875 |  | 52.95%
2022-02-01 22:00 | 44593.9167 |  | 51.96%
2022-02-01 23:00 | 44593.9583 |  | 52.48%
2022-02-02 | 44594 |  | 50.92%
2022-02-02 01:00 | 44594.0417 |  | 50.21%
2022-02-02 02:00 | 44594.0833 |  | 49.71%
2022-02-02 03:00 | 44594.125 |  | 49.74%
2022-02-02 04:00 | 44594.1667 |  | 49.39%
2022-02-02 05:00 | 44594.2083 |  | 49.82%
2022-02-02 06:00 | 44594.25 |  | 52.81%
2022-02-02 07:00 | 44594.2917 |  | 56.53%
2022-02-02 08:00 | 44594.3333 |  | 57.29%
2022-02-02 09:00 | 44594.375 |  | 56.47%
2022-02-02 10:00 | 44594.4167 |  | 56.41%
2022-02-02 11:00 | 44594.4583 |  | 56.71%
2022-02-02 12:00 | 44594.5 |  | 56.76%
2022-02-02 13:00 | 44594.5417 |  | 56.86%
2022-02-02 14:00 | 44594.5833 |  | 57.13%
2022-02-02 15:00 | 44594.625 |  | 57.24%
2022-02-02 16:00 | 44594.6667 |  | 57.22%
2022-02-02 17:00 | 44594.7083 |  | 56.9%
2022-02-02 18:00 | 44594.75 |  | 55.87%
2022-02-02 19:00 | 44594.7917 |  | 55.76%
2022-02-02 20:00 | 44594.8333 |  | 54.02%
2022-02-02 21:00 | 44594.875 |  | 53.83%
2022-02-02 22:00 | 44594.9167 |  | 52.82%
2022-02-02 23:00 | 44594.9583 |  | 53.35%
2022-02-03 | 44595 |  | 51%
2022-02-03 01:00 | 44595.0417 |  | 50.29%
2022-02-03 02:00 | 44595.0833 |  | 49.79%
2022-02-03 03:00 | 44595.125 |  | 49.82%
2022-02-03 04:00 | 44595.1667 |  | 49.47%
2022-02-03 05:00 | 44595.2083 |  | 49.89%
2022-02-03 06:00 | 44595.25 |  | 52.89%
2022-02-03 07:00 | 44595.2917 |  | 56.61%
2022-02-03 08:00 | 44595.3333 |  | 57.38%
2022-02-03 09:00 | 44595.375 |  | 56.56%
2022-02-03 10:00 | 44595.4167 |  | 56.5%
2022-02-03 11:00 | 44595.4583 |  | 56.8%
2022-02-03 12:00 | 44595.5 |  | 56.85%
2022-02-03 13:00 | 44595.5417 |  | 56.95%
2022-02-03 14:00 | 44595.5833 |  | 57.22%
2022-02-03 15:00 | 44595.625 |  | 57.33%
2022-02-03 16:00 | 44595.6667 |  | 57.31%
2022-02-03 17:00 | 44595.7083 |  | 56.99%
2022-02-03 18:00 | 44595.75 |  | 55.95%
2022-02-03 19:00 | 44595.7917 |  | 55.84%
2022-02-03 20:00 | 44595.8333 |  | 54.11%
2022-02-03 21:00 | 44595.875 |  | 53.91%
2022-02-03 22:00 | 44595.9167 |  | 52.9%
2022-02-03 23:00 | 44595.9583 |  | 53.44%
2022-02-04 | 44596 |  | 51.57%
2022-02-04 01:00 | 44596.0417 |  | 50.86%
2022-02-04 02:00 | 44596.0833 |  | 50.36%
2022-02-04 03:00 | 44596.125 |  | 50.39%
2022-02-04 04:00 | 44596.1667 |  | 50.03%
2022-02-04 05:00 | 44596.2083 |  | 50.46%
2022-02-04 06:00 | 44596.25 |  | 53.49%
2022-02-04 07:00 | 44596.2917 |  | 57.26%
2022-02-04 08:00 | 44596.3333 |  | 58.03%
2022-02-04 09:00 | 44596.375 |  | 57.2%
2022-02-04 10:00 | 44596.4167 |  | 57.14%
2022-02-04 11:00 | 44596.4583 |  | 57.44%
2022-02-04 12:00 | 44596.5 |  | 57.5%
2022-02-04 13:00 | 44596.5417 |  | 57.6%
2022-02-04 14:00 | 44596.5833 |  | 57.87%
2022-02-04 15:00 | 44596.625 |  | 57.98%
2022-02-04 16:00 | 44596.6667 |  | 57.96%
2022-02-04 17:00 | 44596.7083 |  | 57.64%
2022-02-04 18:00 | 44596.75 |  | 56.59%
2022-02-04 19:00 | 44596.7917 |  | 56.48%
2022-02-04 20:00 | 44596.8333 |  | 54.72%
2022-02-04 21:00 | 44596.875 |  | 54.53%
2022-02-04 22:00 | 44596.9167 |  | 53.5%
2022-02-04 23:00 | 44596.9583 |  | 54.04%
2022-02-05 | 44597 |  | 50.46%
2022-02-05 01:00 | 44597.0417 |  | 50.16%
2022-02-05 02:00 | 44597.0833 |  | 49.71%
2022-02-05 03:00 | 44597.125 |  | 49.33%
2022-02-05 04:00 | 44597.1667 |  | 49.08%
2022-02-05 05:00 | 44597.2083 |  | 49.35%
2022-02-05 06:00 | 44597.25 |  | 50.03%
2022-02-05 07:00 | 44597.2917 |  | 51.94%
2022-02-05 08:00 | 44597.3333 |  | 54.22%
2022-02-05 09:00 | 44597.375 |  | 55.69%
2022-02-05 10:00 | 44597.4167 |  | 56.24%
2022-02-05 11:00 | 44597.4583 |  | 56.78%
2022-02-05 12:00 | 44597.5 |  | 56.83%
2022-02-05 13:00 | 44597.5417 |  | 56.72%
2022-02-05 14:00 | 44597.5833 |  | 56.06%
2022-02-05 15:00 | 44597.625 |  | 55.59%
2022-02-05 16:00 | 44597.6667 |  | 55%
2022-02-05 17:00 | 44597.7083 |  | 54.94%
2022-02-05 18:00 | 44597.75 |  | 53.73%
2022-02-05 19:00 | 44597.7917 |  | 53.56%
2022-02-05 20:00 | 44597.8333 |  | 51.81%
2022-02-05 21:00 | 44597.875 |  | 50.78%
2022-02-05 22:00 | 44597.9167 |  | 50%
2022-02-05 23:00 | 44597.9583 |  | 50.56%
2022-02-06 | 44598 |  | 49.88%
2022-02-06 01:00 | 44598.0417 |  | 49.59%
2022-02-06 02:00 | 44598.0833 |  | 49.14%
2022-02-06 03:00 | 44598.125 |  | 48.77%
2022-02-06 04:00 | 44598.1667 |  | 48.52%
2022-02-06 05:00 | 44598.2083 |  | 48.78%
2022-02-06 06:00 | 44598.25 |  | 49.46%
2022-02-06 07:00 | 44598.2917 |  | 51.35%
2022-02-06 08:00 | 44598.3333 |  | 53.6%
2022-02-06 09:00 | 44598.375 |  | 55.06%
2022-02-06 10:00 | 44598.4167 |  | 55.6%
2022-02-06 11:00 | 44598.4583 |  | 56.13%
2022-02-06 12:00 | 44598.5 |  | 56.18%
2022-02-06 13:00 | 44598.5417 |  | 56.07%
2022-02-06 14:00 | 44598.5833 |  | 55.41%
2022-02-06 15:00 | 44598.625 |  | 54.95%
2022-02-06 16:00 | 44598.6667 |  | 54.37%
2022-02-06 17:00 | 44598.7083 |  | 54.31%
2022-02-06 18:00 | 44598.75 |  | 53.12%
2022-02-06 19:00 | 44598.7917 |  | 52.95%
2022-02-06 20:00 | 44598.8333 |  | 51.22%
2022-02-06 21:00 | 44598.875 |  | 50.2%
2022-02-06 22:00 | 44598.9167 |  | 49.43%
2022-02-06 23:00 | 44598.9583 |  | 49.98%
2022-02-07 | 44599 |  | 50.99%
2022-02-07 01:00 | 44599.0417 |  | 50.28%
2022-02-07 02:00 | 44599.0833 |  | 49.79%
2022-02-07 03:00 | 44599.125 |  | 49.82%
2022-02-07 04:00 | 44599.1667 |  | 49.46%
2022-02-07 05:00 | 44599.2083 |  | 49.89%
2022-02-07 06:00 | 44599.25 |  | 52.89%
2022-02-07 07:00 | 44599.2917 |  | 56.61%
2022-02-07 08:00 | 44599.3333 |  | 57.37%
2022-02-07 09:00 | 44599.375 |  | 56.55%
2022-02-07 10:00 | 44599.4167 |  | 56.49%
2022-02-07 11:00 | 44599.4583 |  | 56.79%
2022-02-07 12:00 | 44599.5 |  | 56.84%
2022-02-07 13:00 | 44599.5417 |  | 56.94%
2022-02-07 14:00 | 44599.5833 |  | 57.21%
2022-02-07 15:00 | 44599.625 |  | 57.32%
2022-02-07 16:00 | 44599.6667 |  | 57.3%
2022-02-07 17:00 | 44599.7083 |  | 56.99%
2022-02-07 18:00 | 44599.75 |  | 55.95%
2022-02-07 19:00 | 44599.7917 |  | 55.84%
2022-02-07 20:00 | 44599.8333 |  | 54.1%
2022-02-07 21:00 | 44599.875 |  | 53.91%
2022-02-07 22:00 | 44599.9167 |  | 52.9%
2022-02-07 23:00 | 44599.9583 |  | 53.43%
2022-02-08 | 44600 |  | 51.76%
2022-02-08 01:00 | 44600.0417 |  | 51.04%
2022-02-08 02:00 | 44600.0833 |  | 50.54%
2022-02-08 03:00 | 44600.125 |  | 50.57%
2022-02-08 04:00 | 44600.1667 |  | 50.21%
2022-02-08 05:00 | 44600.2083 |  | 50.64%
2022-02-08 06:00 | 44600.25 |  | 53.69%
2022-02-08 07:00 | 44600.2917 |  | 57.46%
2022-02-08 08:00 | 44600.3333 |  | 58.23%
2022-02-08 09:00 | 44600.375 |  | 57.41%
2022-02-08 10:00 | 44600.4167 |  | 57.34%
2022-02-08 11:00 | 44600.4583 |  | 57.65%
2022-02-08 12:00 | 44600.5 |  | 57.7%
2022-02-08 13:00 | 44600.5417 |  | 57.8%
2022-02-08 14:00 | 44600.5833 |  | 58.08%
2022-02-08 15:00 | 44600.625 |  | 58.19%
2022-02-08 16:00 | 44600.6667 |  | 58.16%
2022-02-08 17:00 | 44600.7083 |  | 57.85%
2022-02-08 18:00 | 44600.75 |  | 56.79%
2022-02-08 19:00 | 44600.7917 |  | 56.68%
2022-02-08 20:00 | 44600.8333 |  | 54.92%
2022-02-08 21:00 | 44600.875 |  | 54.72%
2022-02-08 22:00 | 44600.9167 |  | 53.7%
2022-02-08 23:00 | 44600.9583 |  | 54.24%
2022-02-09 | 44601 |  | 51.84%
2022-02-09 01:00 | 44601.0417 |  | 51.12%
2022-02-09 02:00 | 44601.0833 |  | 50.62%
2022-02-09 03:00 | 44601.125 |  | 50.65%
2022-02-09 04:00 | 44601.1667 |  | 50.29%
2022-02-09 05:00 | 44601.2083 |  | 50.72%
2022-02-09 06:00 | 44601.25 |  | 53.77%
2022-02-09 07:00 | 44601.2917 |  | 57.55%
2022-02-09 08:00 | 44601.3333 |  | 58.33%
2022-02-09 09:00 | 44601.375 |  | 57.5%
2022-02-09 10:00 | 44601.4167 |  | 57.43%
2022-02-09 11:00 | 44601.4583 |  | 57.74%
2022-02-09 12:00 | 44601.5 |  | 57.79%
2022-02-09 13:00 | 44601.5417 |  | 57.89%
2022-02-09 14:00 | 44601.5833 |  | 58.17%
2022-02-09 15:00 | 44601.625 |  | 58.28%
2022-02-09 16:00 | 44601.6667 |  | 58.26%
2022-02-09 17:00 | 44601.7083 |  | 57.94%
2022-02-09 18:00 | 44601.75 |  | 56.88%
2022-02-09 19:00 | 44601.7917 |  | 56.77%
2022-02-09 20:00 | 44601.8333 |  | 55%
2022-02-09 21:00 | 44601.875 |  | 54.81%
2022-02-09 22:00 | 44601.9167 |  | 53.78%
2022-02-09 23:00 | 44601.9583 |  | 54.32%
2022-02-10 | 44602 |  | 51.42%
2022-02-10 01:00 | 44602.0417 |  | 50.7%
2022-02-10 02:00 | 44602.0833 |  | 50.21%
2022-02-10 03:00 | 44602.125 |  | 50.24%
2022-02-10 04:00 | 44602.1667 |  | 49.88%
2022-02-10 05:00 | 44602.2083 |  | 50.31%
2022-02-10 06:00 | 44602.25 |  | 53.33%
2022-02-10 07:00 | 44602.2917 |  | 57.08%
2022-02-10 08:00 | 44602.3333 |  | 57.85%
2022-02-10 09:00 | 44602.375 |  | 57.03%
2022-02-10 10:00 | 44602.4167 |  | 56.97%
2022-02-10 11:00 | 44602.4583 |  | 57.27%
2022-02-10 12:00 | 44602.5 |  | 57.32%
2022-02-10 13:00 | 44602.5417 |  | 57.42%
2022-02-10 14:00 | 44602.5833 |  | 57.7%
2022-02-10 15:00 | 44602.625 |  | 57.8%
2022-02-10 16:00 | 44602.6667 |  | 57.78%
2022-02-10 17:00 | 44602.7083 |  | 57.47%
2022-02-10 18:00 | 44602.75 |  | 56.42%
2022-02-10 19:00 | 44602.7917 |  | 56.31%
2022-02-10 20:00 | 44602.8333 |  | 54.56%
2022-02-10 21:00 | 44602.875 |  | 54.36%
2022-02-10 22:00 | 44602.9167 |  | 53.34%
2022-02-10 23:00 | 44602.9583 |  | 53.88%
2022-02-11 | 44603 |  | 51.58%
2022-02-11 01:00 | 44603.0417 |  | 50.87%
2022-02-11 02:00 | 44603.0833 |  | 50.37%
2022-02-11 03:00 | 44603.125 |  | 50.4%
2022-02-11 04:00 | 44603.1667 |  | 50.04%
2022-02-11 05:00 | 44603.2083 |  | 50.47%
2022-02-11 06:00 | 44603.25 |  | 53.5%
2022-02-11 07:00 | 44603.2917 |  | 57.27%
2022-02-11 08:00 | 44603.3333 |  | 58.04%
2022-02-11 09:00 | 44603.375 |  | 57.21%
2022-02-11 10:00 | 44603.4167 |  | 57.15%
2022-02-11 11:00 | 44603.4583 |  | 57.45%
2022-02-11 12:00 | 44603.5 |  | 57.51%
2022-02-11 13:00 | 44603.5417 |  | 57.61%
2022-02-11 14:00 | 44603.5833 |  | 57.88%
2022-02-11 15:00 | 44603.625 |  | 57.99%
2022-02-11 16:00 | 44603.6667 |  | 57.97%
2022-02-11 17:00 | 44603.7083 |  | 57.65%
2022-02-11 18:00 | 44603.75 |  | 56.6%
2022-02-11 19:00 | 44603.7917 |  | 56.49%
2022-02-11 20:00 | 44603.8333 |  | 54.73%
2022-02-11 21:00 | 44603.875 |  | 54.54%
2022-02-11 22:00 | 44603.9167 |  | 53.51%
2022-02-11 23:00 | 44603.9583 |  | 54.05%
2022-02-12 | 44604 |  | 50.72%
2022-02-12 01:00 | 44604.0417 |  | 50.42%
2022-02-12 02:00 | 44604.0833 |  | 49.96%
2022-02-12 03:00 | 44604.125 |  | 49.59%
2022-02-12 04:00 | 44604.1667 |  | 49.33%
2022-02-12 05:00 | 44604.2083 |  | 49.6%
2022-02-12 06:00 | 44604.25 |  | 50.28%
2022-02-12 07:00 | 44604.2917 |  | 52.21%
2022-02-12 08:00 | 44604.3333 |  | 54.49%
2022-02-12 09:00 | 44604.375 |  | 55.98%
2022-02-12 10:00 | 44604.4167 |  | 56.53%
2022-02-12 11:00 | 44604.4583 |  | 57.06%
2022-02-12 12:00 | 44604.5 |  | 57.12%
2022-02-12 13:00 | 44604.5417 |  | 57.01%
2022-02-12 14:00 | 44604.5833 |  | 56.34%
2022-02-12 15:00 | 44604.625 |  | 55.87%
2022-02-12 16:00 | 44604.6667 |  | 55.28%
2022-02-12 17:00 | 44604.7083 |  | 55.22%
2022-02-12 18:00 | 44604.75 |  | 54.01%
2022-02-12 19:00 | 44604.7917 |  | 53.84%
2022-02-12 20:00 | 44604.8333 |  | 52.07%
2022-02-12 21:00 | 44604.875 |  | 51.04%
2022-02-12 22:00 | 44604.9167 |  | 50.26%
2022-02-12 23:00 | 44604.9583 |  | 50.81%
2022-02-13 | 44605 |  | 50.58%
2022-02-13 01:00 | 44605.0417 |  | 50.28%
2022-02-13 02:00 | 44605.0833 |  | 49.83%
2022-02-13 03:00 | 44605.125 |  | 49.45%
2022-02-13 04:00 | 44605.1667 |  | 49.2%
2022-02-13 05:00 | 44605.2083 |  | 49.47%
2022-02-13 06:00 | 44605.25 |  | 50.15%
2022-02-13 07:00 | 44605.2917 |  | 52.06%
2022-02-13 08:00 | 44605.3333 |  | 54.35%
2022-02-13 09:00 | 44605.375 |  | 55.83%
2022-02-13 10:00 | 44605.4167 |  | 56.38%
2022-02-13 11:00 | 44605.4583 |  | 56.91%
2022-02-13 12:00 | 44605.5 |  | 56.96%
2022-02-13 13:00 | 44605.5417 |  | 56.85%
2022-02-13 14:00 | 44605.5833 |  | 56.19%
2022-02-13 15:00 | 44605.625 |  | 55.72%
2022-02-13 16:00 | 44605.6667 |  | 55.13%
2022-02-13 17:00 | 44605.7083 |  | 55.07%
2022-02-13 18:00 | 44605.75 |  | 53.86%
2022-02-13 19:00 | 44605.7917 |  | 53.69%
2022-02-13 20:00 | 44605.8333 |  | 51.93%
2022-02-13 21:00 | 44605.875 |  | 50.9%
2022-02-13 22:00 | 44605.9167 |  | 50.12%
2022-02-13 23:00 | 44605.9583 |  | 50.68%
2022-02-14 | 44606 |  | 51.29%
2022-02-14 01:00 | 44606.0417 |  | 50.57%
2022-02-14 02:00 | 44606.0833 |  | 50.08%
2022-02-14 03:00 | 44606.125 |  | 50.11%
2022-02-14 04:00 | 44606.1667 |  | 49.75%
2022-02-14 05:00 | 44606.2083 |  | 50.18%
2022-02-14 06:00 | 44606.25 |  | 53.2%
2022-02-14 07:00 | 44606.2917 |  | 56.94%
2022-02-14 08:00 | 44606.3333 |  | 57.7%
2022-02-14 09:00 | 44606.375 |  | 56.88%
2022-02-14 10:00 | 44606.4167 |  | 56.82%
2022-02-14 11:00 | 44606.4583 |  | 57.12%
2022-02-14 12:00 | 44606.5 |  | 57.18%
2022-02-14 13:00 | 44606.5417 |  | 57.28%
2022-02-14 14:00 | 44606.5833 |  | 57.55%
2022-02-14 15:00 | 44606.625 |  | 57.66%
2022-02-14 16:00 | 44606.6667 |  | 57.63%
2022-02-14 17:00 | 44606.7083 |  | 57.32%
2022-02-14 18:00 | 44606.75 |  | 56.27%
2022-02-14 19:00 | 44606.7917 |  | 56.16%
2022-02-14 20:00 | 44606.8333 |  | 54.42%
2022-02-14 21:00 | 44606.875 |  | 54.22%
2022-02-14 22:00 | 44606.9167 |  | 53.21%
2022-02-14 23:00 | 44606.9583 |  | 53.74%
2022-02-15 | 44607 |  | 51.12%
2022-02-15 01:00 | 44607.0417 |  | 50.41%
2022-02-15 02:00 | 44607.0833 |  | 49.92%
2022-02-15 03:00 | 44607.125 |  | 49.95%
2022-02-15 04:00 | 44607.1667 |  | 49.6%
2022-02-15 05:00 | 44607.2083 |  | 50.02%
2022-02-15 06:00 | 44607.25 |  | 53.03%
2022-02-15 07:00 | 44607.2917 |  | 56.76%
2022-02-15 08:00 | 44607.3333 |  | 57.52%
2022-02-15 09:00 | 44607.375 |  | 56.7%
2022-02-15 10:00 | 44607.4167 |  | 56.64%
2022-02-15 11:00 | 44607.4583 |  | 56.94%
2022-02-15 12:00 | 44607.5 |  | 56.99%
2022-02-15 13:00 | 44607.5417 |  | 57.09%
2022-02-15 14:00 | 44607.5833 |  | 57.37%
2022-02-15 15:00 | 44607.625 |  | 57.47%
2022-02-15 16:00 | 44607.6667 |  | 57.45%
2022-02-15 17:00 | 44607.7083 |  | 57.14%
2022-02-15 18:00 | 44607.75 |  | 56.1%
2022-02-15 19:00 | 44607.7917 |  | 55.98%
2022-02-15 20:00 | 44607.8333 |  | 54.24%
2022-02-15 21:00 | 44607.875 |  | 54.05%
2022-02-15 22:00 | 44607.9167 |  | 53.04%
2022-02-15 23:00 | 44607.9583 |  | 53.57%
2022-02-16 | 44608 |  | 51.29%
2022-02-16 01:00 | 44608.0417 |  | 50.57%
2022-02-16 02:00 | 44608.0833 |  | 50.08%
2022-02-16 03:00 | 44608.125 |  | 50.11%
2022-02-16 04:00 | 44608.1667 |  | 49.75%
2022-02-16 05:00 | 44608.2083 |  | 50.18%
2022-02-16 06:00 | 44608.25 |  | 53.19%
2022-02-16 07:00 | 44608.2917 |  | 56.94%
2022-02-16 08:00 | 44608.3333 |  | 57.7%
2022-02-16 09:00 | 44608.375 |  | 56.88%
2022-02-16 10:00 | 44608.4167 |  | 56.82%
2022-02-16 11:00 | 44608.4583 |  | 57.12%
2022-02-16 12:00 | 44608.5 |  | 57.17%
2022-02-16 13:00 | 44608.5417 |  | 57.27%
2022-02-16 14:00 | 44608.5833 |  | 57.55%
2022-02-16 15:00 | 44608.625 |  | 57.65%
2022-02-16 16:00 | 44608.6667 |  | 57.63%
2022-02-16 17:00 | 44608.7083 |  | 57.32%
2022-02-16 18:00 | 44608.75 |  | 56.27%
2022-02-16 19:00 | 44608.7917 |  | 56.16%
2022-02-16 20:00 | 44608.8333 |  | 54.41%
2022-02-16 21:00 | 44608.875 |  | 54.22%
2022-02-16 22:00 | 44608.9167 |  | 53.2%
2022-02-16 23:00 | 44608.9583 |  | 53.74%
2022-02-17 | 44609 |  | 51.14%
2022-02-17 01:00 | 44609.0417 |  | 50.43%
2022-02-17 02:00 | 44609.0833 |  | 49.94%
2022-02-17 03:00 | 44609.125 |  | 49.97%
2022-02-17 04:00 | 44609.1667 |  | 49.61%
2022-02-17 05:00 | 44609.2083 |  | 50.04%
2022-02-17 06:00 | 44609.25 |  | 53.05%
2022-02-17 07:00 | 44609.2917 |  | 56.78%
2022-02-17 08:00 | 44609.3333 |  | 57.54%
2022-02-17 09:00 | 44609.375 |  | 56.72%
2022-02-17 10:00 | 44609.4167 |  | 56.66%
2022-02-17 11:00 | 44609.4583 |  | 56.96%
2022-02-17 12:00 | 44609.5 |  | 57.02%
2022-02-17 13:00 | 44609.5417 |  | 57.12%
2022-02-17 14:00 | 44609.5833 |  | 57.39%
2022-02-17 15:00 | 44609.625 |  | 57.49%
2022-02-17 16:00 | 44609.6667 |  | 57.47%
2022-02-17 17:00 | 44609.7083 |  | 57.16%
2022-02-17 18:00 | 44609.75 |  | 56.12%
2022-02-17 19:00 | 44609.7917 |  | 56.01%
2022-02-17 20:00 | 44609.8333 |  | 54.26%
2022-02-17 21:00 | 44609.875 |  | 54.07%
2022-02-17 22:00 | 44609.9167 |  | 53.06%
2022-02-17 23:00 | 44609.9583 |  | 53.59%
2022-02-18 | 44610 |  | 50.7%
2022-02-18 01:00 | 44610.0417 |  | 50%
2022-02-18 02:00 | 44610.0833 |  | 49.5%
2022-02-18 03:00 | 44610.125 |  | 49.54%
2022-02-18 04:00 | 44610.1667 |  | 49.19%
2022-02-18 05:00 | 44610.2083 |  | 49.61%
2022-02-18 06:00 | 44610.25 |  | 52.59%
2022-02-18 07:00 | 44610.2917 |  | 56.29%
2022-02-18 08:00 | 44610.3333 |  | 57.04%
2022-02-18 09:00 | 44610.375 |  | 56.23%
2022-02-18 10:00 | 44610.4167 |  | 56.17%
2022-02-18 11:00 | 44610.4583 |  | 56.47%
2022-02-18 12:00 | 44610.5 |  | 56.52%
2022-02-18 13:00 | 44610.5417 |  | 56.62%
2022-02-18 14:00 | 44610.5833 |  | 56.89%
2022-02-18 15:00 | 44610.625 |  | 57%
2022-02-18 16:00 | 44610.6667 |  | 56.98%
2022-02-18 17:00 | 44610.7083 |  | 56.66%
2022-02-18 18:00 | 44610.75 |  | 55.63%
2022-02-18 19:00 | 44610.7917 |  | 55.52%
2022-02-18 20:00 | 44610.8333 |  | 53.79%
2022-02-18 21:00 | 44610.875 |  | 53.6%
2022-02-18 22:00 | 44610.9167 |  | 52.6%
2022-02-18 23:00 | 44610.9583 |  | 53.13%
2022-02-19 | 44611 |  | 49.09%
2022-02-19 01:00 | 44611.0417 |  | 48.79%
2022-02-19 02:00 | 44611.0833 |  | 48.35%
2022-02-19 03:00 | 44611.125 |  | 47.99%
2022-02-19 04:00 | 44611.1667 |  | 47.75%
2022-02-19 05:00 | 44611.2083 |  | 48.01%
2022-02-19 06:00 | 44611.25 |  | 48.67%
2022-02-19 07:00 | 44611.2917 |  | 50.53%
2022-02-19 08:00 | 44611.3333 |  | 52.74%
2022-02-19 09:00 | 44611.375 |  | 54.18%
2022-02-19 10:00 | 44611.4167 |  | 54.71%
2022-02-19 11:00 | 44611.4583 |  | 55.23%
2022-02-19 12:00 | 44611.5 |  | 55.28%
2022-02-19 13:00 | 44611.5417 |  | 55.17%
2022-02-19 14:00 | 44611.5833 |  | 54.53%
2022-02-19 15:00 | 44611.625 |  | 54.08%
2022-02-19 16:00 | 44611.6667 |  | 53.5%
2022-02-19 17:00 | 44611.7083 |  | 53.44%
2022-02-19 18:00 | 44611.75 |  | 52.27%
2022-02-19 19:00 | 44611.7917 |  | 52.11%
2022-02-19 20:00 | 44611.8333 |  | 50.4%
2022-02-19 21:00 | 44611.875 |  | 49.4%
2022-02-19 22:00 | 44611.9167 |  | 48.64%
2022-02-19 23:00 | 44611.9583 |  | 49.18%
2022-02-20 | 44612 |  | 49.05%
2022-02-20 01:00 | 44612.0417 |  | 48.76%
2022-02-20 02:00 | 44612.0833 |  | 48.32%
2022-02-20 03:00 | 44612.125 |  | 47.96%
2022-02-20 04:00 | 44612.1667 |  | 47.71%
2022-02-20 05:00 | 44612.2083 |  | 47.97%
2022-02-20 06:00 | 44612.25 |  | 48.63%
2022-02-20 07:00 | 44612.2917 |  | 50.49%
2022-02-20 08:00 | 44612.3333 |  | 52.7%
2022-02-20 09:00 | 44612.375 |  | 54.14%
2022-02-20 10:00 | 44612.4167 |  | 54.67%
2022-02-20 11:00 | 44612.4583 |  | 55.19%
2022-02-20 12:00 | 44612.5 |  | 55.24%
2022-02-20 13:00 | 44612.5417 |  | 55.13%
2022-02-20 14:00 | 44612.5833 |  | 54.49%
2022-02-20 15:00 | 44612.625 |  | 54.04%
2022-02-20 16:00 | 44612.6667 |  | 53.46%
2022-02-20 17:00 | 44612.7083 |  | 53.41%
2022-02-20 18:00 | 44612.75 |  | 52.23%
2022-02-20 19:00 | 44612.7917 |  | 52.07%
2022-02-20 20:00 | 44612.8333 |  | 50.36%
2022-02-20 21:00 | 44612.875 |  | 49.36%
2022-02-20 22:00 | 44612.9167 |  | 48.6%
2022-02-20 23:00 | 44612.9583 |  | 49.15%
2022-02-21 | 44613 |  | 49.66%
2022-02-21 01:00 | 44613.0417 |  | 48.97%
2022-02-21 02:00 | 44613.0833 |  | 48.49%
2022-02-21 03:00 | 44613.125 |  | 48.52%
2022-02-21 04:00 | 44613.1667 |  | 48.17%
2022-02-21 05:00 | 44613.2083 |  | 48.58%
2022-02-21 06:00 | 44613.25 |  | 51.5%
2022-02-21 07:00 | 44613.2917 |  | 55.13%
2022-02-21 08:00 | 44613.3333 |  | 55.87%
2022-02-21 09:00 | 44613.375 |  | 55.07%
2022-02-21 10:00 | 44613.4167 |  | 55.01%
2022-02-21 11:00 | 44613.4583 |  | 55.3%
2022-02-21 12:00 | 44613.5 |  | 55.36%
2022-02-21 13:00 | 44613.5417 |  | 55.46%
2022-02-21 14:00 | 44613.5833 |  | 55.72%
2022-02-21 15:00 | 44613.625 |  | 55.82%
2022-02-21 16:00 | 44613.6667 |  | 55.8%
2022-02-21 17:00 | 44613.7083 |  | 55.5%
2022-02-21 18:00 | 44613.75 |  | 54.49%
2022-02-21 19:00 | 44613.7917 |  | 54.38%
2022-02-21 20:00 | 44613.8333 |  | 52.69%
2022-02-21 21:00 | 44613.875 |  | 52.5%
2022-02-21 22:00 | 44613.9167 |  | 51.51%
2022-02-21 23:00 | 44613.9583 |  | 52.04%
2022-02-22 | 44614 |  | 49.78%
2022-02-22 01:00 | 44614.0417 |  | 49.09%
2022-02-22 02:00 | 44614.0833 |  | 48.61%
2022-02-22 03:00 | 44614.125 |  | 48.64%
2022-02-22 04:00 | 44614.1667 |  | 48.29%
2022-02-22 05:00 | 44614.2083 |  | 48.71%
2022-02-22 06:00 | 44614.25 |  | 51.64%
2022-02-22 07:00 | 44614.2917 |  | 55.27%
2022-02-22 08:00 | 44614.3333 |  | 56.01%
2022-02-22 09:00 | 44614.375 |  | 55.21%
2022-02-22 10:00 | 44614.4167 |  | 55.15%
2022-02-22 11:00 | 44614.4583 |  | 55.44%
2022-02-22 12:00 | 44614.5 |  | 55.5%
2022-02-22 13:00 | 44614.5417 |  | 55.6%
2022-02-22 14:00 | 44614.5833 |  | 55.86%
2022-02-22 15:00 | 44614.625 |  | 55.96%
2022-02-22 16:00 | 44614.6667 |  | 55.94%
2022-02-22 17:00 | 44614.7083 |  | 55.64%
2022-02-22 18:00 | 44614.75 |  | 54.62%
2022-02-22 19:00 | 44614.7917 |  | 54.52%
2022-02-22 20:00 | 44614.8333 |  | 52.82%
2022-02-22 21:00 | 44614.875 |  | 52.63%
2022-02-22 22:00 | 44614.9167 |  | 51.65%
2022-02-22 23:00 | 44614.9583 |  | 52.17%
2022-02-23 | 44615 |  | 49.46%
2022-02-23 01:00 | 44615.0417 |  | 48.77%
2022-02-23 02:00 | 44615.0833 |  | 48.3%
2022-02-23 03:00 | 44615.125 |  | 48.33%
2022-02-23 04:00 | 44615.1667 |  | 47.98%
2022-02-23 05:00 | 44615.2083 |  | 48.39%
2022-02-23 06:00 | 44615.25 |  | 51.3%
2022-02-23 07:00 | 44615.2917 |  | 54.91%
2022-02-23 08:00 | 44615.3333 |  | 55.65%
2022-02-23 09:00 | 44615.375 |  | 54.86%
2022-02-23 10:00 | 44615.4167 |  | 54.8%
2022-02-23 11:00 | 44615.4583 |  | 55.09%
2022-02-23 12:00 | 44615.5 |  | 55.14%
2022-02-23 13:00 | 44615.5417 |  | 55.24%
2022-02-23 14:00 | 44615.5833 |  | 55.5%
2022-02-23 15:00 | 44615.625 |  | 55.6%
2022-02-23 16:00 | 44615.6667 |  | 55.58%
2022-02-23 17:00 | 44615.7083 |  | 55.28%
2022-02-23 18:00 | 44615.75 |  | 54.27%
2022-02-23 19:00 | 44615.7917 |  | 54.16%
2022-02-23 20:00 | 44615.8333 |  | 52.48%
2022-02-23 21:00 | 44615.875 |  | 52.29%
2022-02-23 22:00 | 44615.9167 |  | 51.31%
2022-02-23 23:00 | 44615.9583 |  | 51.83%
2022-02-24 | 44616 |  | 48.51%
2022-02-24 01:00 | 44616.0417 |  | 47.4%
2022-02-24 02:00 | 44616.0833 |  | 47.34%
2022-02-24 03:00 | 44616.125 |  | 48.31%
2022-02-24 04:00 | 44616.1667 |  | 49.09%
2022-02-24 05:00 | 44616.2083 |  | 51.02%
2022-02-24 06:00 | 44616.25 |  | 54.93%
2022-02-24 07:00 | 44616.2917 |  | 58.73%
2022-02-24 08:00 | 44616.3333 |  | 58.42%
2022-02-24 09:00 | 44616.375 |  | 57.47%
2022-02-24 10:00 | 44616.4167 |  | 56.83%
2022-02-24 11:00 | 44616.4583 |  | 56.45%
2022-02-24 12:00 | 44616.5 |  | 56.46%
2022-02-24 13:00 | 44616.5417 |  | 56.37%
2022-02-24 14:00 | 44616.5833 |  | 56.17%
2022-02-24 15:00 | 44616.625 |  | 56.13%
2022-02-24 16:00 | 44616.6667 |  | 56.12%
2022-02-24 17:00 | 44616.7083 |  | 56.41%
2022-02-24 18:00 | 44616.75 |  | 56.18%
2022-02-24 19:00 | 44616.7917 |  | 55.45%
2022-02-24 20:00 | 44616.8333 |  | 54.38%
2022-02-24 21:00 | 44616.875 |  | 52.39%
2022-02-24 22:00 | 44616.9167 |  | 51.32%
2022-02-24 23:00 | 44616.9583 |  | 50.48%
2022-02-25 | 44617 |  | 48.87%
2022-02-25 01:00 | 44617.0417 |  | 47.75%
2022-02-25 02:00 | 44617.0833 |  | 47.69%
2022-02-25 03:00 | 44617.125 |  | 48.67%
2022-02-25 04:00 | 44617.1667 |  | 49.45%
2022-02-25 05:00 | 44617.2083 |  | 51.4%
2022-02-25 06:00 | 44617.25 |  | 55.34%
2022-02-25 07:00 | 44617.2917 |  | 59.17%
2022-02-25 08:00 | 44617.3333 |  | 58.85%
2022-02-25 09:00 | 44617.375 |  | 57.89%
2022-02-25 10:00 | 44617.4167 |  | 57.25%
2022-02-25 11:00 | 44617.4583 |  | 56.87%
2022-02-25 12:00 | 44617.5 |  | 56.87%
2022-02-25 13:00 | 44617.5417 |  | 56.79%
2022-02-25 14:00 | 44617.5833 |  | 56.59%
2022-02-25 15:00 | 44617.625 |  | 56.54%
2022-02-25 16:00 | 44617.6667 |  | 56.53%
2022-02-25 17:00 | 44617.7083 |  | 56.83%
2022-02-25 18:00 | 44617.75 |  | 56.59%
2022-02-25 19:00 | 44617.7917 |  | 55.86%
2022-02-25 20:00 | 44617.8333 |  | 54.78%
2022-02-25 21:00 | 44617.875 |  | 52.77%
2022-02-25 22:00 | 44617.9167 |  | 51.7%
2022-02-25 23:00 | 44617.9583 |  | 50.85%
2022-02-26 | 44618 |  | 46.32%
2022-02-26 01:00 | 44618.0417 |  | 46.03%
2022-02-26 02:00 | 44618.0833 |  | 46.51%
2022-02-26 03:00 | 44618.125 |  | 47.2%
2022-02-26 04:00 | 44618.1667 |  | 47.72%
2022-02-26 05:00 | 44618.2083 |  | 49.24%
2022-02-26 06:00 | 44618.25 |  | 51.16%
2022-02-26 07:00 | 44618.2917 |  | 54.48%
2022-02-26 08:00 | 44618.3333 |  | 56.13%
2022-02-26 09:00 | 44618.375 |  | 56.55%
2022-02-26 10:00 | 44618.4167 |  | 56.22%
2022-02-26 11:00 | 44618.4583 |  | 55.54%
2022-02-26 12:00 | 44618.5 |  | 55.54%
2022-02-26 13:00 | 44618.5417 |  | 55.79%
2022-02-26 14:00 | 44618.5833 |  | 54.12%
2022-02-26 15:00 | 44618.625 |  | 52.53%
2022-02-26 16:00 | 44618.6667 |  | 52.36%
2022-02-26 17:00 | 44618.7083 |  | 53.14%
2022-02-26 18:00 | 44618.75 |  | 53.28%
2022-02-26 19:00 | 44618.7917 |  | 53.4%
2022-02-26 20:00 | 44618.8333 |  | 52.41%
2022-02-26 21:00 | 44618.875 |  | 50.16%
2022-02-26 22:00 | 44618.9167 |  | 50.3%
2022-02-26 23:00 | 44618.9583 |  | 50.13%
2022-02-27 | 44619 |  | 46.14%
2022-02-27 01:00 | 44619.0417 |  | 45.86%
2022-02-27 02:00 | 44619.0833 |  | 46.34%
2022-02-27 03:00 | 44619.125 |  | 47.02%
2022-02-27 04:00 | 44619.1667 |  | 47.54%
2022-02-27 05:00 | 44619.2083 |  | 49.05%
2022-02-27 06:00 | 44619.25 |  | 50.96%
2022-02-27 07:00 | 44619.2917 |  | 54.27%
2022-02-27 08:00 | 44619.3333 |  | 55.92%
2022-02-27 09:00 | 44619.375 |  | 56.34%
2022-02-27 10:00 | 44619.4167 |  | 56.01%
2022-02-27 11:00 | 44619.4583 |  | 55.33%
2022-02-27 12:00 | 44619.5 |  | 55.33%
2022-02-27 13:00 | 44619.5417 |  | 55.58%
2022-02-27 14:00 | 44619.5833 |  | 53.91%
2022-02-27 15:00 | 44619.625 |  | 52.33%
2022-02-27 16:00 | 44619.6667 |  | 52.16%
2022-02-27 17:00 | 44619.7083 |  | 52.94%
2022-02-27 18:00 | 44619.75 |  | 53.08%
2022-02-27 19:00 | 44619.7917 |  | 53.19%
2022-02-27 20:00 | 44619.8333 |  | 52.22%
2022-02-27 21:00 | 44619.875 |  | 49.97%
2022-02-27 22:00 | 44619.9167 |  | 50.11%
2022-02-27 23:00 | 44619.9583 |  | 49.94%
2022-02-28 | 44620 |  | 48.57%
2022-02-28 01:00 | 44620.0417 |  | 47.45%
2022-02-28 02:00 | 44620.0833 |  | 47.39%
2022-02-28 03:00 | 44620.125 |  | 48.37%
2022-02-28 04:00 | 44620.1667 |  | 49.15%
2022-02-28 05:00 | 44620.2083 |  | 51.08%
2022-02-28 06:00 | 44620.25 |  | 55%
2022-02-28 07:00 | 44620.2917 |  | 58.8%
2022-02-28 08:00 | 44620.3333 |  | 58.49%
2022-02-28 09:00 | 44620.375 |  | 57.54%
2022-02-28 10:00 | 44620.4167 |  | 56.9%
2022-02-28 11:00 | 44620.4583 |  | 56.52%
2022-02-28 12:00 | 44620.5 |  | 56.52%
2022-02-28 13:00 | 44620.5417 |  | 56.44%
2022-02-28 14:00 | 44620.5833 |  | 56.24%
2022-02-28 15:00 | 44620.625 |  | 56.19%
2022-02-28 16:00 | 44620.6667 |  | 56.18%
2022-02-28 17:00 | 44620.7083 |  | 56.48%
2022-02-28 18:00 | 44620.75 |  | 56.24%
2022-02-28 19:00 | 44620.7917 |  | 55.52%
2022-02-28 20:00 | 44620.8333 |  | 54.44%
2022-02-28 21:00 | 44620.875 |  | 52.45%
2022-02-28 22:00 | 44620.9167 |  | 51.38%
2022-02-28 23:00 | 44620.9583 |  | 50.53%
2022-03-01 | 44621 |  | 48.1%
2022-03-01 01:00 | 44621.0417 |  | 46.99%
2022-03-01 02:00 | 44621.0833 |  | 46.94%
2022-03-01 03:00 | 44621.125 |  | 47.9%
2022-03-01 04:00 | 44621.1667 |  | 48.67%
2022-03-01 05:00 | 44621.2083 |  | 50.59%
2022-03-01 06:00 | 44621.25 |  | 54.46%
2022-03-01 07:00 | 44621.2917 |  | 58.23%
2022-03-01 08:00 | 44621.3333 |  | 57.92%
2022-03-01 09:00 | 44621.375 |  | 56.98%
2022-03-01 10:00 | 44621.4167 |  | 56.35%
2022-03-01 11:00 | 44621.4583 |  | 55.97%
2022-03-01 12:00 | 44621.5 |  | 55.98%
2022-03-01 13:00 | 44621.5417 |  | 55.89%
2022-03-01 14:00 | 44621.5833 |  | 55.69%
2022-03-01 15:00 | 44621.625 |  | 55.65%
2022-03-01 16:00 | 44621.6667 |  | 55.64%
2022-03-01 17:00 | 44621.7083 |  | 55.93%
2022-03-01 18:00 | 44621.75 |  | 55.7%
2022-03-01 19:00 | 44621.7917 |  | 54.98%
2022-03-01 20:00 | 44621.8333 |  | 53.92%
2022-03-01 21:00 | 44621.875 |  | 51.94%
2022-03-01 22:00 | 44621.9167 |  | 50.89%
2022-03-01 23:00 | 44621.9583 |  | 50.05%
2022-03-02 | 44622 |  | 47.61%
2022-03-02 01:00 | 44622.0417 |  | 46.51%
2022-03-02 02:00 | 44622.0833 |  | 46.45%
2022-03-02 03:00 | 44622.125 |  | 47.41%
2022-03-02 04:00 | 44622.1667 |  | 48.17%
2022-03-02 05:00 | 44622.2083 |  | 50.07%
2022-03-02 06:00 | 44622.25 |  | 53.91%
2022-03-02 07:00 | 44622.2917 |  | 57.64%
2022-03-02 08:00 | 44622.3333 |  | 57.33%
2022-03-02 09:00 | 44622.375 |  | 56.39%
2022-03-02 10:00 | 44622.4167 |  | 55.77%
2022-03-02 11:00 | 44622.4583 |  | 55.4%
2022-03-02 12:00 | 44622.5 |  | 55.4%
2022-03-02 13:00 | 44622.5417 |  | 55.32%
2022-03-02 14:00 | 44622.5833 |  | 55.12%
2022-03-02 15:00 | 44622.625 |  | 55.08%
2022-03-02 16:00 | 44622.6667 |  | 55.07%
2022-03-02 17:00 | 44622.7083 |  | 55.36%
2022-03-02 18:00 | 44622.75 |  | 55.13%
2022-03-02 19:00 | 44622.7917 |  | 54.42%
2022-03-02 20:00 | 44622.8333 |  | 53.36%
2022-03-02 21:00 | 44622.875 |  | 51.41%
2022-03-02 22:00 | 44622.9167 |  | 50.36%
2022-03-02 23:00 | 44622.9583 |  | 49.53%
2022-03-03 | 44623 |  | 47.51%
2022-03-03 01:00 | 44623.0417 |  | 46.42%
2022-03-03 02:00 | 44623.0833 |  | 46.37%
2022-03-03 03:00 | 44623.125 |  | 47.32%
2022-03-03 04:00 | 44623.1667 |  | 48.08%
2022-03-03 05:00 | 44623.2083 |  | 49.97%
2022-03-03 06:00 | 44623.25 |  | 53.8%
2022-03-03 07:00 | 44623.2917 |  | 57.53%
2022-03-03 08:00 | 44623.3333 |  | 57.22%
2022-03-03 09:00 | 44623.375 |  | 56.29%
2022-03-03 10:00 | 44623.4167 |  | 55.66%
2022-03-03 11:00 | 44623.4583 |  | 55.29%
2022-03-03 12:00 | 44623.5 |  | 55.3%
2022-03-03 13:00 | 44623.5417 |  | 55.22%
2022-03-03 14:00 | 44623.5833 |  | 55.02%
2022-03-03 15:00 | 44623.625 |  | 54.97%
2022-03-03 16:00 | 44623.6667 |  | 54.96%
2022-03-03 17:00 | 44623.7083 |  | 55.25%
2022-03-03 18:00 | 44623.75 |  | 55.02%
2022-03-03 19:00 | 44623.7917 |  | 54.31%
2022-03-03 20:00 | 44623.8333 |  | 53.26%
2022-03-03 21:00 | 44623.875 |  | 51.31%
2022-03-03 22:00 | 44623.9167 |  | 50.27%
2022-03-03 23:00 | 44623.9583 |  | 49.44%
2022-03-04 | 44624 |  | 47.52%
2022-03-04 01:00 | 44624.0417 |  | 46.42%
2022-03-04 02:00 | 44624.0833 |  | 46.37%
2022-03-04 03:00 | 44624.125 |  | 47.32%
2022-03-04 04:00 | 44624.1667 |  | 48.08%
2022-03-04 05:00 | 44624.2083 |  | 49.98%
2022-03-04 06:00 | 44624.25 |  | 53.8%
2022-03-04 07:00 | 44624.2917 |  | 57.53%
2022-03-04 08:00 | 44624.3333 |  | 57.22%
2022-03-04 09:00 | 44624.375 |  | 56.29%
2022-03-04 10:00 | 44624.4167 |  | 55.66%
2022-03-04 11:00 | 44624.4583 |  | 55.29%
2022-03-04 12:00 | 44624.5 |  | 55.3%
2022-03-04 13:00 | 44624.5417 |  | 55.22%
2022-03-04 14:00 | 44624.5833 |  | 55.02%
2022-03-04 15:00 | 44624.625 |  | 54.97%
2022-03-04 16:00 | 44624.6667 |  | 54.96%
2022-03-04 17:00 | 44624.7083 |  | 55.26%
2022-03-04 18:00 | 44624.75 |  | 55.02%
2022-03-04 19:00 | 44624.7917 |  | 54.32%
2022-03-04 20:00 | 44624.8333 |  | 53.26%
2022-03-04 21:00 | 44624.875 |  | 51.31%
2022-03-04 22:00 | 44624.9167 |  | 50.27%
2022-03-04 23:00 | 44624.9583 |  | 49.44%
2022-03-05 | 44625 |  | 44.61%
2022-03-05 01:00 | 44625.0417 |  | 44.34%
2022-03-05 02:00 | 44625.0833 |  | 44.8%
2022-03-05 03:00 | 44625.125 |  | 45.46%
2022-03-05 04:00 | 44625.1667 |  | 45.96%
2022-03-05 05:00 | 44625.2083 |  | 47.42%
2022-03-05 06:00 | 44625.25 |  | 49.27%
2022-03-05 07:00 | 44625.2917 |  | 52.47%
2022-03-05 08:00 | 44625.3333 |  | 54.06%
2022-03-05 09:00 | 44625.375 |  | 54.46%
2022-03-05 10:00 | 44625.4167 |  | 54.15%
2022-03-05 11:00 | 44625.4583 |  | 53.49%
2022-03-05 12:00 | 44625.5 |  | 53.49%
2022-03-05 13:00 | 44625.5417 |  | 53.74%
2022-03-05 14:00 | 44625.5833 |  | 52.12%
2022-03-05 15:00 | 44625.625 |  | 50.6%
2022-03-05 16:00 | 44625.6667 |  | 50.43%
2022-03-05 17:00 | 44625.7083 |  | 51.18%
2022-03-05 18:00 | 44625.75 |  | 51.32%
2022-03-05 19:00 | 44625.7917 |  | 51.43%
2022-03-05 20:00 | 44625.8333 |  | 50.48%
2022-03-05 21:00 | 44625.875 |  | 48.31%
2022-03-05 22:00 | 44625.9167 |  | 48.44%
2022-03-05 23:00 | 44625.9583 |  | 48.28%
2022-03-06 | 44626 |  | 44.72%
2022-03-06 01:00 | 44626.0417 |  | 44.45%
2022-03-06 02:00 | 44626.0833 |  | 44.91%
2022-03-06 03:00 | 44626.125 |  | 45.57%
2022-03-06 04:00 | 44626.1667 |  | 46.07%
2022-03-06 05:00 | 44626.2083 |  | 47.54%
2022-03-06 06:00 | 44626.25 |  | 49.39%
2022-03-06 07:00 | 44626.2917 |  | 52.6%
2022-03-06 08:00 | 44626.3333 |  | 54.2%
2022-03-06 09:00 | 44626.375 |  | 54.6%
2022-03-06 10:00 | 44626.4167 |  | 54.28%
2022-03-06 11:00 | 44626.4583 |  | 53.63%
2022-03-06 12:00 | 44626.5 |  | 53.62%
2022-03-06 13:00 | 44626.5417 |  | 53.87%
2022-03-06 14:00 | 44626.5833 |  | 52.25%
2022-03-06 15:00 | 44626.625 |  | 50.72%
2022-03-06 16:00 | 44626.6667 |  | 50.56%
2022-03-06 17:00 | 44626.7083 |  | 51.31%
2022-03-06 18:00 | 44626.75 |  | 51.44%
2022-03-06 19:00 | 44626.7917 |  | 51.55%
2022-03-06 20:00 | 44626.8333 |  | 50.61%
2022-03-06 21:00 | 44626.875 |  | 48.43%
2022-03-06 22:00 | 44626.9167 |  | 48.56%
2022-03-06 23:00 | 44626.9583 |  | 48.4%
2022-03-07 | 44627 |  | 47.73%
2022-03-07 01:00 | 44627.0417 |  | 46.63%
2022-03-07 02:00 | 44627.0833 |  | 46.58%
2022-03-07 03:00 | 44627.125 |  | 47.53%
2022-03-07 04:00 | 44627.1667 |  | 48.3%
2022-03-07 05:00 | 44627.2083 |  | 50.2%
2022-03-07 06:00 | 44627.25 |  | 54.05%
2022-03-07 07:00 | 44627.2917 |  | 57.79%
2022-03-07 08:00 | 44627.3333 |  | 57.48%
2022-03-07 09:00 | 44627.375 |  | 56.54%
2022-03-07 10:00 | 44627.4167 |  | 55.91%
2022-03-07 11:00 | 44627.4583 |  | 55.54%
2022-03-07 12:00 | 44627.5 |  | 55.55%
2022-03-07 13:00 | 44627.5417 |  | 55.47%
2022-03-07 14:00 | 44627.5833 |  | 55.27%
2022-03-07 15:00 | 44627.625 |  | 55.22%
2022-03-07 16:00 | 44627.6667 |  | 55.21%
2022-03-07 17:00 | 44627.7083 |  | 55.51%
2022-03-07 18:00 | 44627.75 |  | 55.27%
2022-03-07 19:00 | 44627.7917 |  | 54.56%
2022-03-07 20:00 | 44627.8333 |  | 53.5%
2022-03-07 21:00 | 44627.875 |  | 51.54%
2022-03-07 22:00 | 44627.9167 |  | 50.5%
2022-03-07 23:00 | 44627.9583 |  | 49.66%
2022-03-08 | 44628 |  | 47.73%
2022-03-08 01:00 | 44628.0417 |  | 46.63%
2022-03-08 02:00 | 44628.0833 |  | 46.58%
2022-03-08 03:00 | 44628.125 |  | 47.53%
2022-03-08 04:00 | 44628.1667 |  | 48.3%
2022-03-08 05:00 | 44628.2083 |  | 50.2%
2022-03-08 06:00 | 44628.25 |  | 54.05%
2022-03-08 07:00 | 44628.2917 |  | 57.79%
2022-03-08 08:00 | 44628.3333 |  | 57.48%
2022-03-08 09:00 | 44628.375 |  | 56.54%
2022-03-08 10:00 | 44628.4167 |  | 55.91%
2022-03-08 11:00 | 44628.4583 |  | 55.54%
2022-03-08 12:00 | 44628.5 |  | 55.55%
2022-03-08 13:00 | 44628.5417 |  | 55.47%
2022-03-08 14:00 | 44628.5833 |  | 55.27%
2022-03-08 15:00 | 44628.625 |  | 55.22%
2022-03-08 16:00 | 44628.6667 |  | 55.21%
2022-03-08 17:00 | 44628.7083 |  | 55.51%
2022-03-08 18:00 | 44628.75 |  | 55.27%
2022-03-08 19:00 | 44628.7917 |  | 54.56%
2022-03-08 20:00 | 44628.8333 |  | 53.5%
2022-03-08 21:00 | 44628.875 |  | 51.54%
2022-03-08 22:00 | 44628.9167 |  | 50.5%
2022-03-08 23:00 | 44628.9583 |  | 49.66%
2022-03-09 | 44629 |  | 47.48%
2022-03-09 01:00 | 44629.0417 |  | 46.38%
2022-03-09 02:00 | 44629.0833 |  | 46.33%
2022-03-09 03:00 | 44629.125 |  | 47.28%
2022-03-09 04:00 | 44629.1667 |  | 48.04%
2022-03-09 05:00 | 44629.2083 |  | 49.93%
2022-03-09 06:00 | 44629.25 |  | 53.76%
2022-03-09 07:00 | 44629.2917 |  | 57.48%
2022-03-09 08:00 | 44629.3333 |  | 57.17%
2022-03-09 09:00 | 44629.375 |  | 56.24%
2022-03-09 10:00 | 44629.4167 |  | 55.62%
2022-03-09 11:00 | 44629.4583 |  | 55.24%
2022-03-09 12:00 | 44629.5 |  | 55.25%
2022-03-09 13:00 | 44629.5417 |  | 55.17%
2022-03-09 14:00 | 44629.5833 |  | 54.97%
2022-03-09 15:00 | 44629.625 |  | 54.93%
2022-03-09 16:00 | 44629.6667 |  | 54.92%
2022-03-09 17:00 | 44629.7083 |  | 55.21%
2022-03-09 18:00 | 44629.75 |  | 54.98%
2022-03-09 19:00 | 44629.7917 |  | 54.27%
2022-03-09 20:00 | 44629.8333 |  | 53.22%
2022-03-09 21:00 | 44629.875 |  | 51.27%
2022-03-09 22:00 | 44629.9167 |  | 50.23%
2022-03-09 23:00 | 44629.9583 |  | 49.4%
2022-03-10 | 44630 |  | 46.76%
2022-03-10 01:00 | 44630.0417 |  | 45.68%
2022-03-10 02:00 | 44630.0833 |  | 45.63%
2022-03-10 03:00 | 44630.125 |  | 46.57%
2022-03-10 04:00 | 44630.1667 |  | 47.31%
2022-03-10 05:00 | 44630.2083 |  | 49.18%
2022-03-10 06:00 | 44630.25 |  | 52.94%
2022-03-10 07:00 | 44630.2917 |  | 56.61%
2022-03-10 08:00 | 44630.3333 |  | 56.31%
2022-03-10 09:00 | 44630.375 |  | 55.39%
2022-03-10 10:00 | 44630.4167 |  | 54.77%
2022-03-10 11:00 | 44630.4583 |  | 54.41%
2022-03-10 12:00 | 44630.5 |  | 54.41%
2022-03-10 13:00 | 44630.5417 |  | 54.33%
2022-03-10 14:00 | 44630.5833 |  | 54.14%
2022-03-10 15:00 | 44630.625 |  | 54.1%
2022-03-10 16:00 | 44630.6667 |  | 54.09%
2022-03-10 17:00 | 44630.7083 |  | 54.37%
2022-03-10 18:00 | 44630.75 |  | 54.14%
2022-03-10 19:00 | 44630.7917 |  | 53.45%
2022-03-10 20:00 | 44630.8333 |  | 52.41%
2022-03-10 21:00 | 44630.875 |  | 50.49%
2022-03-10 22:00 | 44630.9167 |  | 49.47%
2022-03-10 23:00 | 44630.9583 |  | 48.65%
2022-03-11 | 44631 |  | 46.3%
2022-03-11 01:00 | 44631.0417 |  | 45.24%
2022-03-11 02:00 | 44631.0833 |  | 45.18%
2022-03-11 03:00 | 44631.125 |  | 46.11%
2022-03-11 04:00 | 44631.1667 |  | 46.85%
2022-03-11 05:00 | 44631.2083 |  | 48.7%
2022-03-11 06:00 | 44631.25 |  | 52.43%
2022-03-11 07:00 | 44631.2917 |  | 56.06%
2022-03-11 08:00 | 44631.3333 |  | 55.76%
2022-03-11 09:00 | 44631.375 |  | 54.85%
2022-03-11 10:00 | 44631.4167 |  | 54.24%
2022-03-11 11:00 | 44631.4583 |  | 53.88%
2022-03-11 12:00 | 44631.5 |  | 53.88%
2022-03-11 13:00 | 44631.5417 |  | 53.8%
2022-03-11 14:00 | 44631.5833 |  | 53.61%
2022-03-11 15:00 | 44631.625 |  | 53.57%
2022-03-11 16:00 | 44631.6667 |  | 53.56%
2022-03-11 17:00 | 44631.7083 |  | 53.84%
2022-03-11 18:00 | 44631.75 |  | 53.62%
2022-03-11 19:00 | 44631.7917 |  | 52.93%
2022-03-11 20:00 | 44631.8333 |  | 51.9%
2022-03-11 21:00 | 44631.875 |  | 50%
2022-03-11 22:00 | 44631.9167 |  | 48.98%
2022-03-11 23:00 | 44631.9583 |  | 48.17%
2022-03-12 | 44632 |  | 43.4%
2022-03-12 01:00 | 44632.0417 |  | 43.13%
2022-03-12 02:00 | 44632.0833 |  | 43.58%
2022-03-12 03:00 | 44632.125 |  | 44.22%
2022-03-12 04:00 | 44632.1667 |  | 44.71%
2022-03-12 05:00 | 44632.2083 |  | 46.13%
2022-03-12 06:00 | 44632.25 |  | 47.93%
2022-03-12 07:00 | 44632.2917 |  | 51.04%
2022-03-12 08:00 | 44632.3333 |  | 52.59%
2022-03-12 09:00 | 44632.375 |  | 52.98%
2022-03-12 10:00 | 44632.4167 |  | 52.67%
2022-03-12 11:00 | 44632.4583 |  | 52.04%
2022-03-12 12:00 | 44632.5 |  | 52.03%
2022-03-12 13:00 | 44632.5417 |  | 52.27%
2022-03-12 14:00 | 44632.5833 |  | 50.7%
2022-03-12 15:00 | 44632.625 |  | 49.22%
2022-03-12 16:00 | 44632.6667 |  | 49.06%
2022-03-12 17:00 | 44632.7083 |  | 49.79%
2022-03-12 18:00 | 44632.75 |  | 49.92%
2022-03-12 19:00 | 44632.7917 |  | 50.03%
2022-03-12 20:00 | 44632.8333 |  | 49.11%
2022-03-12 21:00 | 44632.875 |  | 46.99%
2022-03-12 22:00 | 44632.9167 |  | 47.12%
2022-03-12 23:00 | 44632.9583 |  | 46.97%
2022-03-13 | 44633 |  | 43.58%
2022-03-13 01:00 | 44633.0417 |  | 43.31%
2022-03-13 02:00 | 44633.0833 |  | 43.76%
2022-03-13 03:00 | 44633.125 |  | 44.41%
2022-03-13 04:00 | 44633.1667 |  | 44.9%
2022-03-13 05:00 | 44633.2083 |  | 46.33%
2022-03-13 06:00 | 44633.25 |  | 48.13%
2022-03-13 07:00 | 44633.2917 |  | 51.26%
2022-03-13 08:00 | 44633.3333 |  | 52.82%
2022-03-13 09:00 | 44633.375 |  | 53.21%
2022-03-13 10:00 | 44633.4167 |  | 52.9%
2022-03-13 11:00 | 44633.4583 |  | 52.26%
2022-03-13 12:00 | 44633.5 |  | 52.26%
2022-03-13 13:00 | 44633.5417 |  | 52.5%
2022-03-13 14:00 | 44633.5833 |  | 50.92%
2022-03-13 15:00 | 44633.625 |  | 49.43%
2022-03-13 16:00 | 44633.6667 |  | 49.27%
2022-03-13 17:00 | 44633.7083 |  | 50%
2022-03-13 18:00 | 44633.75 |  | 50.13%
2022-03-13 19:00 | 44633.7917 |  | 50.24%
2022-03-13 20:00 | 44633.8333 |  | 49.32%
2022-03-13 21:00 | 44633.875 |  | 47.19%
2022-03-13 22:00 | 44633.9167 |  | 47.33%
2022-03-13 23:00 | 44633.9583 |  | 47.17%
2022-03-14 | 44634 |  | 47.04%
2022-03-14 01:00 | 44634.0417 |  | 45.96%
2022-03-14 02:00 | 44634.0833 |  | 45.9%
2022-03-14 03:00 | 44634.125 |  | 46.85%
2022-03-14 04:00 | 44634.1667 |  | 47.6%
2022-03-14 05:00 | 44634.2083 |  | 49.47%
2022-03-14 06:00 | 44634.25 |  | 53.26%
2022-03-14 07:00 | 44634.2917 |  | 56.95%
2022-03-14 08:00 | 44634.3333 |  | 56.64%
2022-03-14 09:00 | 44634.375 |  | 55.72%
2022-03-14 10:00 | 44634.4167 |  | 55.1%
2022-03-14 11:00 | 44634.4583 |  | 54.73%
2022-03-14 12:00 | 44634.5 |  | 54.74%
2022-03-14 13:00 | 44634.5417 |  | 54.66%
2022-03-14 14:00 | 44634.5833 |  | 54.47%
2022-03-14 15:00 | 44634.625 |  | 54.42%
2022-03-14 16:00 | 44634.6667 |  | 54.41%
2022-03-14 17:00 | 44634.7083 |  | 54.7%
2022-03-14 18:00 | 44634.75 |  | 54.47%
2022-03-14 19:00 | 44634.7917 |  | 53.77%
2022-03-14 20:00 | 44634.8333 |  | 52.73%
2022-03-14 21:00 | 44634.875 |  | 50.79%
2022-03-14 22:00 | 44634.9167 |  | 49.76%
2022-03-14 23:00 | 44634.9583 |  | 48.94%
2022-03-15 | 44635 |  | 47.09%
2022-03-15 01:00 | 44635.0417 |  | 46.01%
2022-03-15 02:00 | 44635.0833 |  | 45.96%
2022-03-15 03:00 | 44635.125 |  | 46.9%
2022-03-15 04:00 | 44635.1667 |  | 47.65%
2022-03-15 05:00 | 44635.2083 |  | 49.53%
2022-03-15 06:00 | 44635.25 |  | 53.33%
2022-03-15 07:00 | 44635.2917 |  | 57.02%
2022-03-15 08:00 | 44635.3333 |  | 56.71%
2022-03-15 09:00 | 44635.375 |  | 55.79%
2022-03-15 10:00 | 44635.4167 |  | 55.17%
2022-03-15 11:00 | 44635.4583 |  | 54.8%
2022-03-15 12:00 | 44635.5 |  | 54.81%
2022-03-15 13:00 | 44635.5417 |  | 54.73%
2022-03-15 14:00 | 44635.5833 |  | 54.53%
2022-03-15 15:00 | 44635.625 |  | 54.48%
2022-03-15 16:00 | 44635.6667 |  | 54.47%
2022-03-15 17:00 | 44635.7083 |  | 54.76%
2022-03-15 18:00 | 44635.75 |  | 54.53%
2022-03-15 19:00 | 44635.7917 |  | 53.83%
2022-03-15 20:00 | 44635.8333 |  | 52.79%
2022-03-15 21:00 | 44635.875 |  | 50.85%
2022-03-15 22:00 | 44635.9167 |  | 49.82%
2022-03-15 23:00 | 44635.9583 |  | 49%
2022-03-16 | 44636 |  | 47.11%
2022-03-16 01:00 | 44636.0417 |  | 46.03%
2022-03-16 02:00 | 44636.0833 |  | 45.97%
2022-03-16 03:00 | 44636.125 |  | 46.92%
2022-03-16 04:00 | 44636.1667 |  | 47.67%
2022-03-16 05:00 | 44636.2083 |  | 49.55%
2022-03-16 06:00 | 44636.25 |  | 53.34%
2022-03-16 07:00 | 44636.2917 |  | 57.04%
2022-03-16 08:00 | 44636.3333 |  | 56.73%
2022-03-16 09:00 | 44636.375 |  | 55.81%
2022-03-16 10:00 | 44636.4167 |  | 55.19%
2022-03-16 11:00 | 44636.4583 |  | 54.82%
2022-03-16 12:00 | 44636.5 |  | 54.82%
2022-03-16 13:00 | 44636.5417 |  | 54.74%
2022-03-16 14:00 | 44636.5833 |  | 54.55%
2022-03-16 15:00 | 44636.625 |  | 54.5%
2022-03-16 16:00 | 44636.6667 |  | 54.49%
2022-03-16 17:00 | 44636.7083 |  | 54.78%
2022-03-16 18:00 | 44636.75 |  | 54.55%
2022-03-16 19:00 | 44636.7917 |  | 53.85%
2022-03-16 20:00 | 44636.8333 |  | 52.81%
2022-03-16 21:00 | 44636.875 |  | 50.87%
2022-03-16 22:00 | 44636.9167 |  | 49.84%
2022-03-16 23:00 | 44636.9583 |  | 49.02%
2022-03-17 | 44637 |  | 47.05%
2022-03-17 01:00 | 44637.0417 |  | 45.97%
2022-03-17 02:00 | 44637.0833 |  | 45.91%
2022-03-17 03:00 | 44637.125 |  | 46.86%
2022-03-17 04:00 | 44637.1667 |  | 47.61%
2022-03-17 05:00 | 44637.2083 |  | 49.49%
2022-03-17 06:00 | 44637.25 |  | 53.28%
2022-03-17 07:00 | 44637.2917 |  | 56.96%
2022-03-17 08:00 | 44637.3333 |  | 56.66%
2022-03-17 09:00 | 44637.375 |  | 55.74%
2022-03-17 10:00 | 44637.4167 |  | 55.12%
2022-03-17 11:00 | 44637.4583 |  | 54.75%
2022-03-17 12:00 | 44637.5 |  | 54.76%
2022-03-17 13:00 | 44637.5417 |  | 54.68%
2022-03-17 14:00 | 44637.5833 |  | 54.48%
2022-03-17 15:00 | 44637.625 |  | 54.43%
2022-03-17 16:00 | 44637.6667 |  | 54.42%
2022-03-17 17:00 | 44637.7083 |  | 54.71%
2022-03-17 18:00 | 44637.75 |  | 54.48%
2022-03-17 19:00 | 44637.7917 |  | 53.78%
2022-03-17 20:00 | 44637.8333 |  | 52.74%
2022-03-17 21:00 | 44637.875 |  | 50.81%
2022-03-17 22:00 | 44637.9167 |  | 49.78%
2022-03-17 23:00 | 44637.9583 |  | 48.95%
2022-03-18 | 44638 |  | 46.73%
2022-03-18 01:00 | 44638.0417 |  | 45.66%
2022-03-18 02:00 | 44638.0833 |  | 45.6%
2022-03-18 03:00 | 44638.125 |  | 46.54%
2022-03-18 04:00 | 44638.1667 |  | 47.29%
2022-03-18 05:00 | 44638.2083 |  | 49.15%
2022-03-18 06:00 | 44638.25 |  | 52.92%
2022-03-18 07:00 | 44638.2917 |  | 56.58%
2022-03-18 08:00 | 44638.3333 |  | 56.28%
2022-03-18 09:00 | 44638.375 |  | 55.36%
2022-03-18 10:00 | 44638.4167 |  | 54.75%
2022-03-18 11:00 | 44638.4583 |  | 54.38%
2022-03-18 12:00 | 44638.5 |  | 54.39%
2022-03-18 13:00 | 44638.5417 |  | 54.31%
2022-03-18 14:00 | 44638.5833 |  | 54.11%
2022-03-18 15:00 | 44638.625 |  | 54.07%
2022-03-18 16:00 | 44638.6667 |  | 54.06%
2022-03-18 17:00 | 44638.7083 |  | 54.35%
2022-03-18 18:00 | 44638.75 |  | 54.12%
2022-03-18 19:00 | 44638.7917 |  | 53.42%
2022-03-18 20:00 | 44638.8333 |  | 52.38%
2022-03-18 21:00 | 44638.875 |  | 50.47%
2022-03-18 22:00 | 44638.9167 |  | 49.44%
2022-03-18 23:00 | 44638.9583 |  | 48.62%
2022-03-19 | 44639 |  | 43.58%
2022-03-19 01:00 | 44639.0417 |  | 43.31%
2022-03-19 02:00 | 44639.0833 |  | 43.76%
2022-03-19 03:00 | 44639.125 |  | 44.4%
2022-03-19 04:00 | 44639.1667 |  | 44.89%
2022-03-19 05:00 | 44639.2083 |  | 46.32%
2022-03-19 06:00 | 44639.25 |  | 48.13%
2022-03-19 07:00 | 44639.2917 |  | 51.25%
2022-03-19 08:00 | 44639.3333 |  | 52.81%
2022-03-19 09:00 | 44639.375 |  | 53.2%
2022-03-19 10:00 | 44639.4167 |  | 52.89%
2022-03-19 11:00 | 44639.4583 |  | 52.25%
2022-03-19 12:00 | 44639.5 |  | 52.25%
2022-03-19 13:00 | 44639.5417 |  | 52.49%
2022-03-19 14:00 | 44639.5833 |  | 50.91%
2022-03-19 15:00 | 44639.625 |  | 49.42%
2022-03-19 16:00 | 44639.6667 |  | 49.26%
2022-03-19 17:00 | 44639.7083 |  | 50%
2022-03-19 18:00 | 44639.75 |  | 50.12%
2022-03-19 19:00 | 44639.7917 |  | 50.23%
2022-03-19 20:00 | 44639.8333 |  | 49.31%
2022-03-19 21:00 | 44639.875 |  | 47.19%
2022-03-19 22:00 | 44639.9167 |  | 47.32%
2022-03-19 23:00 | 44639.9583 |  | 47.16%
2022-03-20 | 44640 |  | 43.7%
2022-03-20 01:00 | 44640.0417 |  | 43.43%
2022-03-20 02:00 | 44640.0833 |  | 43.88%
2022-03-20 03:00 | 44640.125 |  | 44.52%
2022-03-20 04:00 | 44640.1667 |  | 45.02%
2022-03-20 05:00 | 44640.2083 |  | 46.45%
2022-03-20 06:00 | 44640.25 |  | 48.26%
2022-03-20 07:00 | 44640.2917 |  | 51.39%
2022-03-20 08:00 | 44640.3333 |  | 52.95%
2022-03-20 09:00 | 44640.375 |  | 53.35%
2022-03-20 10:00 | 44640.4167 |  | 53.03%
2022-03-20 11:00 | 44640.4583 |  | 52.4%
2022-03-20 12:00 | 44640.5 |  | 52.39%
2022-03-20 13:00 | 44640.5417 |  | 52.63%
2022-03-20 14:00 | 44640.5833 |  | 51.05%
2022-03-20 15:00 | 44640.625 |  | 49.56%
2022-03-20 16:00 | 44640.6667 |  | 49.4%
2022-03-20 17:00 | 44640.7083 |  | 50.13%
2022-03-20 18:00 | 44640.75 |  | 50.26%
2022-03-20 19:00 | 44640.7917 |  | 50.37%
2022-03-20 20:00 | 44640.8333 |  | 49.45%
2022-03-20 21:00 | 44640.875 |  | 47.32%
2022-03-20 22:00 | 44640.9167 |  | 47.45%
2022-03-20 23:00 | 44640.9583 |  | 47.29%
2022-03-21 | 44641 |  | 46.66%
2022-03-21 01:00 | 44641.0417 |  | 45.58%
2022-03-21 02:00 | 44641.0833 |  | 45.53%
2022-03-21 03:00 | 44641.125 |  | 46.46%
2022-03-21 04:00 | 44641.1667 |  | 47.21%
2022-03-21 05:00 | 44641.2083 |  | 49.07%
2022-03-21 06:00 | 44641.25 |  | 52.83%
2022-03-21 07:00 | 44641.2917 |  | 56.49%
2022-03-21 08:00 | 44641.3333 |  | 56.18%
2022-03-21 09:00 | 44641.375 |  | 55.27%
2022-03-21 10:00 | 44641.4167 |  | 54.66%
2022-03-21 11:00 | 44641.4583 |  | 54.29%
2022-03-21 12:00 | 44641.5 |  | 54.3%
2022-03-21 13:00 | 44641.5417 |  | 54.22%
2022-03-21 14:00 | 44641.5833 |  | 54.02%
2022-03-21 15:00 | 44641.625 |  | 53.98%
2022-03-21 16:00 | 44641.6667 |  | 53.97%
2022-03-21 17:00 | 44641.7083 |  | 54.26%
2022-03-21 18:00 | 44641.75 |  | 54.03%
2022-03-21 19:00 | 44641.7917 |  | 53.33%
2022-03-21 20:00 | 44641.8333 |  | 52.3%
2022-03-21 21:00 | 44641.875 |  | 50.38%
2022-03-21 22:00 | 44641.9167 |  | 49.36%
2022-03-21 23:00 | 44641.9583 |  | 48.54%
2022-03-22 | 44642 |  | 46.52%
2022-03-22 01:00 | 44642.0417 |  | 45.46%
2022-03-22 02:00 | 44642.0833 |  | 45.4%
2022-03-22 03:00 | 44642.125 |  | 46.33%
2022-03-22 04:00 | 44642.1667 |  | 47.08%
2022-03-22 05:00 | 44642.2083 |  | 48.93%
2022-03-22 06:00 | 44642.25 |  | 52.68%
2022-03-22 07:00 | 44642.2917 |  | 56.33%
2022-03-22 08:00 | 44642.3333 |  | 56.03%
2022-03-22 09:00 | 44642.375 |  | 55.11%
2022-03-22 10:00 | 44642.4167 |  | 54.5%
2022-03-22 11:00 | 44642.4583 |  | 54.14%
2022-03-22 12:00 | 44642.5 |  | 54.14%
2022-03-22 13:00 | 44642.5417 |  | 54.06%
2022-03-22 14:00 | 44642.5833 |  | 53.87%
2022-03-22 15:00 | 44642.625 |  | 53.83%
2022-03-22 16:00 | 44642.6667 |  | 53.82%
2022-03-22 17:00 | 44642.7083 |  | 54.1%
2022-03-22 18:00 | 44642.75 |  | 53.88%
2022-03-22 19:00 | 44642.7917 |  | 53.18%
2022-03-22 20:00 | 44642.8333 |  | 52.15%
2022-03-22 21:00 | 44642.875 |  | 50.24%
2022-03-22 22:00 | 44642.9167 |  | 49.22%
2022-03-22 23:00 | 44642.9583 |  | 48.41%
2022-03-23 | 44643 |  | 46.53%
2022-03-23 01:00 | 44643.0417 |  | 45.47%
2022-03-23 02:00 | 44643.0833 |  | 45.41%
2022-03-23 03:00 | 44643.125 |  | 46.34%
2022-03-23 04:00 | 44643.1667 |  | 47.09%
2022-03-23 05:00 | 44643.2083 |  | 48.94%
2022-03-23 06:00 | 44643.25 |  | 52.69%
2022-03-23 07:00 | 44643.2917 |  | 56.34%
2022-03-23 08:00 | 44643.3333 |  | 56.04%
2022-03-23 09:00 | 44643.375 |  | 55.13%
2022-03-23 10:00 | 44643.4167 |  | 54.51%
2022-03-23 11:00 | 44643.4583 |  | 54.15%
2022-03-23 12:00 | 44643.5 |  | 54.16%
2022-03-23 13:00 | 44643.5417 |  | 54.08%
2022-03-23 14:00 | 44643.5833 |  | 53.88%
2022-03-23 15:00 | 44643.625 |  | 53.84%
2022-03-23 16:00 | 44643.6667 |  | 53.83%
2022-03-23 17:00 | 44643.7083 |  | 54.12%
2022-03-23 18:00 | 44643.75 |  | 53.89%
2022-03-23 19:00 | 44643.7917 |  | 53.19%
2022-03-23 20:00 | 44643.8333 |  | 52.16%
2022-03-23 21:00 | 44643.875 |  | 50.25%
2022-03-23 22:00 | 44643.9167 |  | 49.23%
2022-03-23 23:00 | 44643.9583 |  | 48.42%
2022-03-24 | 44644 |  | 46.23%
2022-03-24 01:00 | 44644.0417 |  | 45.17%
2022-03-24 02:00 | 44644.0833 |  | 45.12%
2022-03-24 03:00 | 44644.125 |  | 46.04%
2022-03-24 04:00 | 44644.1667 |  | 46.78%
2022-03-24 05:00 | 44644.2083 |  | 48.63%
2022-03-24 06:00 | 44644.25 |  | 52.35%
2022-03-24 07:00 | 44644.2917 |  | 55.98%
2022-03-24 08:00 | 44644.3333 |  | 55.68%
2022-03-24 09:00 | 44644.375 |  | 54.77%
2022-03-24 10:00 | 44644.4167 |  | 54.16%
2022-03-24 11:00 | 44644.4583 |  | 53.8%
2022-03-24 12:00 | 44644.5 |  | 53.81%
2022-03-24 13:00 | 44644.5417 |  | 53.73%
2022-03-24 14:00 | 44644.5833 |  | 53.53%
2022-03-24 15:00 | 44644.625 |  | 53.49%
2022-03-24 16:00 | 44644.6667 |  | 53.48%
2022-03-24 17:00 | 44644.7083 |  | 53.77%
2022-03-24 18:00 | 44644.75 |  | 53.54%
2022-03-24 19:00 | 44644.7917 |  | 52.85%
2022-03-24 20:00 | 44644.8333 |  | 51.83%
2022-03-24 21:00 | 44644.875 |  | 49.93%
2022-03-24 22:00 | 44644.9167 |  | 48.91%
2022-03-24 23:00 | 44644.9583 |  | 48.11%
2022-03-25 | 44645 |  | 45.68%
2022-03-25 01:00 | 44645.0417 |  | 44.63%
2022-03-25 02:00 | 44645.0833 |  | 44.58%
2022-03-25 03:00 | 44645.125 |  | 45.5%
2022-03-25 04:00 | 44645.1667 |  | 46.22%
2022-03-25 05:00 | 44645.2083 |  | 48.05%
2022-03-25 06:00 | 44645.25 |  | 51.73%
2022-03-25 07:00 | 44645.2917 |  | 55.31%
2022-03-25 08:00 | 44645.3333 |  | 55.01%
2022-03-25 09:00 | 44645.375 |  | 54.12%
2022-03-25 10:00 | 44645.4167 |  | 53.52%
2022-03-25 11:00 | 44645.4583 |  | 53.16%
2022-03-25 12:00 | 44645.5 |  | 53.16%
2022-03-25 13:00 | 44645.5417 |  | 53.09%
2022-03-25 14:00 | 44645.5833 |  | 52.9%
2022-03-25 15:00 | 44645.625 |  | 52.85%
2022-03-25 16:00 | 44645.6667 |  | 52.84%
2022-03-25 17:00 | 44645.7083 |  | 53.12%
2022-03-25 18:00 | 44645.75 |  | 52.9%
2022-03-25 19:00 | 44645.7917 |  | 52.22%
2022-03-25 20:00 | 44645.8333 |  | 51.21%
2022-03-25 21:00 | 44645.875 |  | 49.33%
2022-03-25 22:00 | 44645.9167 |  | 48.33%
2022-03-25 23:00 | 44645.9583 |  | 47.53%
2022-03-26 | 44646 |  | 42.2%
2022-03-26 01:00 | 44646.0417 |  | 41.94%
2022-03-26 02:00 | 44646.0833 |  | 42.37%
2022-03-26 03:00 | 44646.125 |  | 43%
2022-03-26 04:00 | 44646.1667 |  | 43.47%
2022-03-26 05:00 | 44646.2083 |  | 44.86%
2022-03-26 06:00 | 44646.25 |  | 46.61%
2022-03-26 07:00 | 44646.2917 |  | 49.63%
2022-03-26 08:00 | 44646.3333 |  | 51.14%
2022-03-26 09:00 | 44646.375 |  | 51.52%
2022-03-26 10:00 | 44646.4167 |  | 51.22%
2022-03-26 11:00 | 44646.4583 |  | 50.6%
2022-03-26 12:00 | 44646.5 |  | 50.6%
2022-03-26 13:00 | 44646.5417 |  | 50.83%
2022-03-26 14:00 | 44646.5833 |  | 49.3%
2022-03-26 15:00 | 44646.625 |  | 47.86%
2022-03-26 16:00 | 44646.6667 |  | 47.7%
2022-03-26 17:00 | 44646.7083 |  | 48.42%
2022-03-26 18:00 | 44646.75 |  | 48.54%
2022-03-26 19:00 | 44646.7917 |  | 48.64%
2022-03-26 20:00 | 44646.8333 |  | 47.75%
2022-03-26 21:00 | 44646.875 |  | 45.69%
2022-03-26 22:00 | 44646.9167 |  | 45.82%
2022-03-26 23:00 | 44646.9583 |  | 45.67%
2022-03-27 | 44647 |  | 40.2%
2022-03-27 01:00 | 44647.0417 |  | 38.75%
2022-03-27 02:00 | 44647.0833 |  | 38.51%
2022-03-27 03:00 | 44647.125 |  | 39.01%
2022-03-27 04:00 | 44647.1667 |  | 40.69%
2022-03-27 05:00 | 44647.2083 |  | 44.15%
2022-03-27 06:00 | 44647.25 |  | 47.81%
2022-03-27 07:00 | 44647.2917 |  | 50.75%
2022-03-27 08:00 | 44647.3333 |  | 51.91%
2022-03-27 09:00 | 44647.375 |  | 50.77%
2022-03-27 10:00 | 44647.4167 |  | 49.68%
2022-03-27 11:00 | 44647.4583 |  | 49.41%
2022-03-27 12:00 | 44647.5 |  | 49.05%
2022-03-27 13:00 | 44647.5417 |  | 47.77%
2022-03-27 14:00 | 44647.5833 |  | 47.05%
2022-03-27 15:00 | 44647.625 |  | 46.1%
2022-03-27 16:00 | 44647.6667 |  | 46.63%
2022-03-27 17:00 | 44647.7083 |  | 46.52%
2022-03-27 18:00 | 44647.75 |  | 46.7%
2022-03-27 19:00 | 44647.7917 |  | 45.87%
2022-03-27 20:00 | 44647.8333 |  | 46.48%
2022-03-27 21:00 | 44647.875 |  | 45.15%
2022-03-27 22:00 | 44647.9167 |  | 44.06%
2022-03-27 23:00 | 44647.9583 |  | 39.81%
2022-03-28 | 44648 |  | 40.09%
2022-03-28 01:00 | 44648.0417 |  | 39.97%
2022-03-28 02:00 | 44648.0833 |  | 39.97%
2022-03-28 03:00 | 44648.125 |  | 40.89%
2022-03-28 04:00 | 44648.1667 |  | 42.85%
2022-03-28 05:00 | 44648.2083 |  | 47.14%
2022-03-28 06:00 | 44648.25 |  | 51.89%
2022-03-28 07:00 | 44648.2917 |  | 52.92%
2022-03-28 08:00 | 44648.3333 |  | 52.86%
2022-03-28 09:00 | 44648.375 |  | 51.95%
2022-03-28 10:00 | 44648.4167 |  | 51.63%
2022-03-28 11:00 | 44648.4583 |  | 51.8%
2022-03-28 12:00 | 44648.5 |  | 51.75%
2022-03-28 13:00 | 44648.5417 |  | 51.4%
2022-03-28 14:00 | 44648.5833 |  | 51.37%
2022-03-28 15:00 | 44648.625 |  | 51.28%
2022-03-28 16:00 | 44648.6667 |  | 51.04%
2022-03-28 17:00 | 44648.7083 |  | 50.99%
2022-03-28 18:00 | 44648.75 |  | 50.31%
2022-03-28 19:00 | 44648.7917 |  | 49.08%
2022-03-28 20:00 | 44648.8333 |  | 48.4%
2022-03-28 21:00 | 44648.875 |  | 47.29%
2022-03-28 22:00 | 44648.9167 |  | 46.78%
2022-03-28 23:00 | 44648.9583 |  | 42.55%
2022-03-29 | 44649 |  | 40.09%
2022-03-29 01:00 | 44649.0417 |  | 39.97%
2022-03-29 02:00 | 44649.0833 |  | 39.97%
2022-03-29 03:00 | 44649.125 |  | 40.89%
2022-03-29 04:00 | 44649.1667 |  | 42.85%
2022-03-29 05:00 | 44649.2083 |  | 47.14%
2022-03-29 06:00 | 44649.25 |  | 51.89%
2022-03-29 07:00 | 44649.2917 |  | 52.92%
2022-03-29 08:00 | 44649.3333 |  | 52.86%
2022-03-29 09:00 | 44649.375 |  | 51.95%
2022-03-29 10:00 | 44649.4167 |  | 51.63%
2022-03-29 11:00 | 44649.4583 |  | 51.8%
2022-03-29 12:00 | 44649.5 |  | 51.75%
2022-03-29 13:00 | 44649.5417 |  | 51.4%
2022-03-29 14:00 | 44649.5833 |  | 51.37%
2022-03-29 15:00 | 44649.625 |  | 51.28%
2022-03-29 16:00 | 44649.6667 |  | 51.04%
2022-03-29 17:00 | 44649.7083 |  | 50.99%
2022-03-29 18:00 | 44649.75 |  | 50.31%
2022-03-29 19:00 | 44649.7917 |  | 49.08%
2022-03-29 20:00 | 44649.8333 |  | 48.4%
2022-03-29 21:00 | 44649.875 |  | 47.29%
2022-03-29 22:00 | 44649.9167 |  | 46.78%
2022-03-29 23:00 | 44649.9583 |  | 42.55%
2022-03-30 | 44650 |  | 40.75%
2022-03-30 01:00 | 44650.0417 |  | 40.63%
2022-03-30 02:00 | 44650.0833 |  | 40.62%
2022-03-30 03:00 | 44650.125 |  | 41.56%
2022-03-30 04:00 | 44650.1667 |  | 43.55%
2022-03-30 05:00 | 44650.2083 |  | 47.91%
2022-03-30 06:00 | 44650.25 |  | 52.74%
2022-03-30 07:00 | 44650.2917 |  | 53.79%
2022-03-30 08:00 | 44650.3333 |  | 53.73%
2022-03-30 09:00 | 44650.375 |  | 52.8%
2022-03-30 10:00 | 44650.4167 |  | 52.47%
2022-03-30 11:00 | 44650.4583 |  | 52.65%
2022-03-30 12:00 | 44650.5 |  | 52.59%
2022-03-30 13:00 | 44650.5417 |  | 52.24%
2022-03-30 14:00 | 44650.5833 |  | 52.21%
2022-03-30 15:00 | 44650.625 |  | 52.12%
2022-03-30 16:00 | 44650.6667 |  | 51.88%
2022-03-30 17:00 | 44650.7083 |  | 51.83%
2022-03-30 18:00 | 44650.75 |  | 51.14%
2022-03-30 19:00 | 44650.7917 |  | 49.89%
2022-03-30 20:00 | 44650.8333 |  | 49.2%
2022-03-30 21:00 | 44650.875 |  | 48.07%
2022-03-30 22:00 | 44650.9167 |  | 47.54%
2022-03-30 23:00 | 44650.9583 |  | 43.24%
2022-03-31 | 44651 |  | 41.01%
2022-03-31 01:00 | 44651.0417 |  | 40.89%
2022-03-31 02:00 | 44651.0833 |  | 40.88%
2022-03-31 03:00 | 44651.125 |  | 41.82%
2022-03-31 04:00 | 44651.1667 |  | 43.83%
2022-03-31 05:00 | 44651.2083 |  | 48.22%
2022-03-31 06:00 | 44651.25 |  | 53.08%
2022-03-31 07:00 | 44651.2917 |  | 54.13%
2022-03-31 08:00 | 44651.3333 |  | 54.07%
2022-03-31 09:00 | 44651.375 |  | 53.14%
2022-03-31 10:00 | 44651.4167 |  | 52.81%
2022-03-31 11:00 | 44651.4583 |  | 52.98%
2022-03-31 12:00 | 44651.5 |  | 52.93%
2022-03-31 13:00 | 44651.5417 |  | 52.58%
2022-03-31 14:00 | 44651.5833 |  | 52.55%
2022-03-31 15:00 | 44651.625 |  | 52.46%
2022-03-31 16:00 | 44651.6667 |  | 52.21%
2022-03-31 17:00 | 44651.7083 |  | 52.16%
2022-03-31 18:00 | 44651.75 |  | 51.47%
2022-03-31 19:00 | 44651.7917 |  | 50.2%
2022-03-31 20:00 | 44651.8333 |  | 49.51%
2022-03-31 21:00 | 44651.875 |  | 48.38%
2022-03-31 22:00 | 44651.9167 |  | 47.85%
2022-03-31 23:00 | 44651.9583 |  | 43.52%
Formulas:
Date = [Date, row above]+1/24

## 1.6 Forced outage rates
1.6 Forced outage rates
Average forced outage rate over 2010-2019
Nuclear | 3.7%
Classical | 8%
CCGT | 9%
GT | 9.6%
TJ | 3.6%
Waste | 1%
CHP | 6.8%
Pumped storage | 4.4%
HVDC link | 6%

## 2.1 Demand
2.1 Demand
The projections were made in the context of the total demand electricity forecasting framework using the tool developped by Climact for the strategic reserve study
Further details can be consulted on the following link:
https://app.powerbi.com/view?r=eyJrIjoiNTdkMzUzNmMtMGIwMy00YTJlLThhZDAtMTc0ZTE1OTU4ZjdlIiwidCI6ImUxZDBhZDNjLTk0MmItNDkyOC05MDgyLTU5NzgxMWRkYTAwZiIsImMiOjh9&pageName=ReportSectionfe23cb0f5c5771a5168d
|  | Historical values |  | Base case normalized total demand
|  | Total demand [TWh] | Normalised total demand [TWh] | Growth rate | Forecast [TWh]
historical | 2019 | 84.942 | 85.7
forecast | 2020 |  |  | -4.3% | 82
forecast | 2021 |  |  | 3.7% | 85
forecast | 2022 |  |  | 2.1% | 86.8
forecast | 2023 |  |  | 0.2% | 87

## 2.2 Demand profile
2.2 Demand profile
Normalised hourly demand [MW]
Date | Hour
2021-11-01 | 44501 | 8515.124
2021-11-01 01:00 | 44501.0417 | 8094.634
2021-11-01 02:00 | 44501.0833 | 7808.934
2021-11-01 03:00 | 44501.125 | 7640.984
2021-11-01 04:00 | 44501.1667 | 7554.999
2021-11-01 05:00 | 44501.2083 | 7804.184
2021-11-01 06:00 | 44501.25 | 8199.958
2021-11-01 07:00 | 44501.2917 | 8615.505
2021-11-01 08:00 | 44501.3333 | 9046.294
2021-11-01 09:00 | 44501.375 | 9281.865
2021-11-01 10:00 | 44501.4167 | 9568.205
2021-11-01 11:00 | 44501.4583 | 9433.378
2021-11-01 12:00 | 44501.5 | 9265.711
2021-11-01 13:00 | 44501.5417 | 9089.982
2021-11-01 14:00 | 44501.5833 | 9058.173
2021-11-01 15:00 | 44501.625 | 9123.762
2021-11-01 16:00 | 44501.6667 | 9730.438
2021-11-01 17:00 | 44501.7083 | 10103.92
2021-11-01 18:00 | 44501.75 | 10038.21
2021-11-01 19:00 | 44501.7917 | 9721.844
2021-11-01 20:00 | 44501.8333 | 9285.145
2021-11-01 21:00 | 44501.875 | 9507.79
2021-11-01 22:00 | 44501.9167 | 9517.837
2021-11-01 23:00 | 44501.9583 | 8958.817
2021-11-02 | 44502 | 9242.612
2021-11-02 01:00 | 44502.0417 | 8858.98
2021-11-02 02:00 | 44502.0833 | 8704.925
2021-11-02 03:00 | 44502.125 | 8742.439
2021-11-02 04:00 | 44502.1667 | 9244.291
2021-11-02 05:00 | 44502.2083 | 10264.64
2021-11-02 06:00 | 44502.25 | 11000.94
2021-11-02 07:00 | 44502.2917 | 11327.41
2021-11-02 08:00 | 44502.3333 | 11555.63
2021-11-02 09:00 | 44502.375 | 11671
2021-11-02 10:00 | 44502.4167 | 11735.56
2021-11-02 11:00 | 44502.4583 | 11586.88
2021-11-02 12:00 | 44502.5 | 11551.25
2021-11-02 13:00 | 44502.5417 | 11438.42
2021-11-02 14:00 | 44502.5833 | 11410.22
2021-11-02 15:00 | 44502.625 | 11452.91
2021-11-02 16:00 | 44502.6667 | 11952.39
2021-11-02 17:00 | 44502.7083 | 12058.28
2021-11-02 18:00 | 44502.75 | 11689.65
2021-11-02 19:00 | 44502.7917 | 11095.78
2021-11-02 20:00 | 44502.8333 | 10623.34
2021-11-02 21:00 | 44502.875 | 10771.5
2021-11-02 22:00 | 44502.9167 | 10615.64
2021-11-02 23:00 | 44502.9583 | 9920.404
2021-11-03 | 44503 | 9237.149
2021-11-03 01:00 | 44503.0417 | 8848.501
2021-11-03 02:00 | 44503.0833 | 8690.464
2021-11-03 03:00 | 44503.125 | 8723.089
2021-11-03 04:00 | 44503.1667 | 9231.587
2021-11-03 05:00 | 44503.2083 | 10270.35
2021-11-03 06:00 | 44503.25 | 11017.86
2021-11-03 07:00 | 44503.2917 | 11341.06
2021-11-03 08:00 | 44503.3333 | 11567.04
2021-11-03 09:00 | 44503.375 | 11678.56
2021-11-03 10:00 | 44503.4167 | 11746.48
2021-11-03 11:00 | 44503.4583 | 11598.44
2021-11-03 12:00 | 44503.5 | 11567.98
2021-11-03 13:00 | 44503.5417 | 11456.76
2021-11-03 14:00 | 44503.5833 | 11429.76
2021-11-03 15:00 | 44503.625 | 11471.45
2021-11-03 16:00 | 44503.6667 | 11982.42
2021-11-03 17:00 | 44503.7083 | 12089.84
2021-11-03 18:00 | 44503.75 | 11707.69
2021-11-03 19:00 | 44503.7917 | 11098.47
2021-11-03 20:00 | 44503.8333 | 10609.88
2021-11-03 21:00 | 44503.875 | 10769.58
2021-11-03 22:00 | 44503.9167 | 10626.13
2021-11-03 23:00 | 44503.9583 | 9924.883
2021-11-04 | 44504 | 9218.7
2021-11-04 01:00 | 44504.0417 | 8825.597
2021-11-04 02:00 | 44504.0833 | 8664.738
2021-11-04 03:00 | 44504.125 | 8698.008
2021-11-04 04:00 | 44504.1667 | 9209.042
2021-11-04 05:00 | 44504.2083 | 10260.09
2021-11-04 06:00 | 44504.25 | 11016.2
2021-11-04 07:00 | 44504.2917 | 11340.84
2021-11-04 08:00 | 44504.3333 | 11568.45
2021-11-04 09:00 | 44504.375 | 11680.2
2021-11-04 10:00 | 44504.4167 | 11749.68
2021-11-04 11:00 | 44504.4583 | 11600.92
2021-11-04 12:00 | 44504.5 | 11571.79
2021-11-04 13:00 | 44504.5417 | 11459.02
2021-11-04 14:00 | 44504.5833 | 11432.35
2021-11-04 15:00 | 44504.625 | 11474.29
2021-11-04 16:00 | 44504.6667 | 11993.58
2021-11-04 17:00 | 44504.7083 | 12103.15
2021-11-04 18:00 | 44504.75 | 11713.9
2021-11-04 19:00 | 44504.7917 | 11095.5
2021-11-04 20:00 | 44504.8333 | 10597.88
2021-11-04 21:00 | 44504.875 | 10762.68
2021-11-04 22:00 | 44504.9167 | 10622.52
2021-11-04 23:00 | 44504.9583 | 9914.199
2021-11-05 | 44505 | 9242.654
2021-11-05 01:00 | 44505.0417 | 8853.152
2021-11-05 02:00 | 44505.0833 | 8694.951
2021-11-05 03:00 | 44505.125 | 8729.424
2021-11-05 04:00 | 44505.1667 | 9241.824
2021-11-05 05:00 | 44505.2083 | 10287.84
2021-11-05 06:00 | 44505.25 | 11039.4
2021-11-05 07:00 | 44505.2917 | 11362.48
2021-11-05 08:00 | 44505.3333 | 11587.76
2021-11-05 09:00 | 44505.375 | 11698.86
2021-11-05 10:00 | 44505.4167 | 11766.33
2021-11-05 11:00 | 44505.4583 | 11618.14
2021-11-05 12:00 | 44505.5 | 11588.73
2021-11-05 13:00 | 44505.5417 | 11476.02
2021-11-05 14:00 | 44505.5833 | 11449.25
2021-11-05 15:00 | 44505.625 | 11491.09
2021-11-05 16:00 | 44505.6667 | 12004.02
2021-11-05 17:00 | 44505.7083 | 12110.54
2021-11-05 18:00 | 44505.75 | 11724.85
2021-11-05 19:00 | 44505.7917 | 11111.83
2021-11-05 20:00 | 44505.8333 | 10620.79
2021-11-05 21:00 | 44505.875 | 10781.32
2021-11-05 22:00 | 44505.9167 | 10637.74
2021-11-05 23:00 | 44505.9583 | 9933.95
2021-11-06 | 44506 | 9015.743
2021-11-06 01:00 | 44506.0417 | 8647.888
2021-11-06 02:00 | 44506.0833 | 8403.653
2021-11-06 03:00 | 44506.125 | 8302.027
2021-11-06 04:00 | 44506.1667 | 8283.584
2021-11-06 05:00 | 44506.2083 | 8618.946
2021-11-06 06:00 | 44506.25 | 9017.891
2021-11-06 07:00 | 44506.2917 | 9359.375
2021-11-06 08:00 | 44506.3333 | 9701.931
2021-11-06 09:00 | 44506.375 | 9884.03
2021-11-06 10:00 | 44506.4167 | 10109.29
2021-11-06 11:00 | 44506.4583 | 9992.274
2021-11-06 12:00 | 44506.5 | 9872.041
2021-11-06 13:00 | 44506.5417 | 9730.198
2021-11-06 14:00 | 44506.5833 | 9706.342
2021-11-06 15:00 | 44506.625 | 9757.682
2021-11-06 16:00 | 44506.6667 | 10283.31
2021-11-06 17:00 | 44506.7083 | 10567.6
2021-11-06 18:00 | 44506.75 | 10469.66
2021-11-06 19:00 | 44506.7917 | 10135.81
2021-11-06 20:00 | 44506.8333 | 9731.891
2021-11-06 21:00 | 44506.875 | 9934.419
2021-11-06 22:00 | 44506.9167 | 9945.757
2021-11-06 23:00 | 44506.9583 | 9441.961
2021-11-07 | 44507 | 8578.984
2021-11-07 01:00 | 44507.0417 | 8147.597
2021-11-07 02:00 | 44507.0833 | 7852.943
2021-11-07 03:00 | 44507.125 | 7682.38
2021-11-07 04:00 | 44507.1667 | 7586.77
2021-11-07 05:00 | 44507.2083 | 7824.274
2021-11-07 06:00 | 44507.25 | 8224.604
2021-11-07 07:00 | 44507.2917 | 8657.711
2021-11-07 08:00 | 44507.3333 | 9105.945
2021-11-07 09:00 | 44507.375 | 9353.156
2021-11-07 10:00 | 44507.4167 | 9650.228
2021-11-07 11:00 | 44507.4583 | 9510.571
2021-11-07 12:00 | 44507.5 | 9332.407
2021-11-07 13:00 | 44507.5417 | 9149.966
2021-11-07 14:00 | 44507.5833 | 9115.466
2021-11-07 15:00 | 44507.625 | 9183.762
2021-11-07 16:00 | 44507.6667 | 9804.531
2021-11-07 17:00 | 44507.7083 | 10194.87
2021-11-07 18:00 | 44507.75 | 10135.44
2021-11-07 19:00 | 44507.7917 | 9820.121
2021-11-07 20:00 | 44507.8333 | 9379.376
2021-11-07 21:00 | 44507.875 | 9601.742
2021-11-07 22:00 | 44507.9167 | 9603.683
2021-11-07 23:00 | 44507.9583 | 9029.413
2021-11-08 | 44508 | 9272.682
2021-11-08 01:00 | 44508.0417 | 8883.473
2021-11-08 02:00 | 44508.0833 | 8724.229
2021-11-08 03:00 | 44508.125 | 8756.201
2021-11-08 04:00 | 44508.1667 | 9266.396
2021-11-08 05:00 | 44508.2083 | 10316.4
2021-11-08 06:00 | 44508.25 | 11068.72
2021-11-08 07:00 | 44508.2917 | 11384.85
2021-11-08 08:00 | 44508.3333 | 11605.11
2021-11-08 09:00 | 44508.375 | 11711.42
2021-11-08 10:00 | 44508.4167 | 11780.63
2021-11-08 11:00 | 44508.4583 | 11634.86
2021-11-08 12:00 | 44508.5 | 11610.58
2021-11-08 13:00 | 44508.5417 | 11499.56
2021-11-08 14:00 | 44508.5833 | 11474.31
2021-11-08 15:00 | 44508.625 | 11514.75
2021-11-08 16:00 | 44508.6667 | 12031.29
2021-11-08 17:00 | 44508.7083 | 12137.15
2021-11-08 18:00 | 44508.75 | 11744.77
2021-11-08 19:00 | 44508.7917 | 11125.87
2021-11-08 20:00 | 44508.8333 | 10627.05
2021-11-08 21:00 | 44508.875 | 10795.59
2021-11-08 22:00 | 44508.9167 | 10664.47
2021-11-08 23:00 | 44508.9583 | 9964.18
2021-11-09 | 44509 | 9323.853
2021-11-09 01:00 | 44509.0417 | 8938.122
2021-11-09 02:00 | 44509.0833 | 8781.043
2021-11-09 03:00 | 44509.125 | 8815.22
2021-11-09 04:00 | 44509.1667 | 9317.207
2021-11-09 05:00 | 44509.2083 | 10351.9
2021-11-09 06:00 | 44509.25 | 11094.99
2021-11-09 07:00 | 44509.2917 | 11412.19
2021-11-09 08:00 | 44509.3333 | 11633.34
2021-11-09 09:00 | 44509.375 | 11741.31
2021-11-09 10:00 | 44509.4167 | 11810.05
2021-11-09 11:00 | 44509.4583 | 11664.46
2021-11-09 12:00 | 44509.5 | 11637.15
2021-11-09 13:00 | 44509.5417 | 11526.77
2021-11-09 14:00 | 44509.5833 | 11500.79
2021-11-09 15:00 | 44509.625 | 11541.39
2021-11-09 16:00 | 44509.6667 | 12050.51
2021-11-09 17:00 | 44509.7083 | 12156.18
2021-11-09 18:00 | 44509.75 | 11773.2
2021-11-09 19:00 | 44509.7917 | 11165.02
2021-11-09 20:00 | 44509.8333 | 10676.04
2021-11-09 21:00 | 44509.875 | 10838.6
2021-11-09 22:00 | 44509.9167 | 10702.38
2021-11-09 23:00 | 44509.9583 | 10007.88
2021-11-10 | 44510 | 9352.522
2021-11-10 01:00 | 44510.0417 | 8961.853
2021-11-10 02:00 | 44510.0833 | 8799.73
2021-11-10 03:00 | 44510.125 | 8827.918
2021-11-10 04:00 | 44510.1667 | 9324.179
2021-11-10 05:00 | 44510.2083 | 10364.4
2021-11-10 06:00 | 44510.25 | 11112.35
2021-11-10 07:00 | 44510.2917 | 11427.37
2021-11-10 08:00 | 44510.3333 | 11649.37
2021-11-10 09:00 | 44510.375 | 11755.74
2021-11-10 10:00 | 44510.4167 | 11830.32
2021-11-10 11:00 | 44510.4583 | 11685.69
2021-11-10 12:00 | 44510.5 | 11661.39
2021-11-10 13:00 | 44510.5417 | 11550.68
2021-11-10 14:00 | 44510.5833 | 11526
2021-11-10 15:00 | 44510.625 | 11566.18
2021-11-10 16:00 | 44510.6667 | 12087.61
2021-11-10 17:00 | 44510.7083 | 12198.61
2021-11-10 18:00 | 44510.75 | 11807.88
2021-11-10 19:00 | 44510.7917 | 11189.73
2021-11-10 20:00 | 44510.8333 | 10686.42
2021-11-10 21:00 | 44510.875 | 10860.95
2021-11-10 22:00 | 44510.9167 | 10739.24
2021-11-10 23:00 | 44510.9583 | 10041.8
2021-11-11 | 44511 | 8578.984
2021-11-11 01:00 | 44511.0417 | 8147.597
2021-11-11 02:00 | 44511.0833 | 7852.943
2021-11-11 03:00 | 44511.125 | 7682.38
2021-11-11 04:00 | 44511.1667 | 7586.77
2021-11-11 05:00 | 44511.2083 | 7824.274
2021-11-11 06:00 | 44511.25 | 8224.604
2021-11-11 07:00 | 44511.2917 | 8657.711
2021-11-11 08:00 | 44511.3333 | 9105.945
2021-11-11 09:00 | 44511.375 | 9353.156
2021-11-11 10:00 | 44511.4167 | 9650.228
2021-11-11 11:00 | 44511.4583 | 9510.571
2021-11-11 12:00 | 44511.5 | 9332.407
2021-11-11 13:00 | 44511.5417 | 9149.966
2021-11-11 14:00 | 44511.5833 | 9115.466
2021-11-11 15:00 | 44511.625 | 9183.762
2021-11-11 16:00 | 44511.6667 | 9804.531
2021-11-11 17:00 | 44511.7083 | 10194.87
2021-11-11 18:00 | 44511.75 | 10135.44
2021-11-11 19:00 | 44511.7917 | 9820.121
2021-11-11 20:00 | 44511.8333 | 9379.376
2021-11-11 21:00 | 44511.875 | 9601.742
2021-11-11 22:00 | 44511.9167 | 9603.683
2021-11-11 23:00 | 44511.9583 | 9029.413
2021-11-12 | 44512 | 9404.576
2021-11-12 01:00 | 44512.0417 | 9006.59
2021-11-12 02:00 | 44512.0833 | 8838.376
2021-11-12 03:00 | 44512.125 | 8864.426
2021-11-12 04:00 | 44512.1667 | 9361.218
2021-11-12 05:00 | 44512.2083 | 10423.9
2021-11-12 06:00 | 44512.25 | 11186.12
2021-11-12 07:00 | 44512.2917 | 11497.17
2021-11-12 08:00 | 44512.3333 | 11717.06
2021-11-12 09:00 | 44512.375 | 11818.51
2021-11-12 10:00 | 44512.4167 | 11898.92
2021-11-12 11:00 | 44512.4583 | 11755.27
2021-11-12 12:00 | 44512.5 | 11737.6
2021-11-12 13:00 | 44512.5417 | 11628.56
2021-11-12 14:00 | 44512.5833 | 11605.67
2021-11-12 15:00 | 44512.625 | 11644.53
2021-11-12 16:00 | 44512.6667 | 12182.75
2021-11-12 17:00 | 44512.7083 | 12297.3
2021-11-12 18:00 | 44512.75 | 11889.14
2021-11-12 19:00 | 44512.7917 | 11250.69
2021-11-12 20:00 | 44512.8333 | 10724.82
2021-11-12 21:00 | 44512.875 | 10915.91
2021-11-12 22:00 | 44512.9167 | 10812.32
2021-11-12 23:00 | 44512.9583 | 10106.84
2021-11-13 | 44513 | 9195.961
2021-11-13 01:00 | 44513.0417 | 8825.794
2021-11-13 02:00 | 44513.0833 | 8583.538
2021-11-13 03:00 | 44513.125 | 8492.233
2021-11-13 04:00 | 44513.1667 | 8484.213
2021-11-13 05:00 | 44513.2083 | 8840.067
2021-11-13 06:00 | 44513.25 | 9249.563
2021-11-13 07:00 | 44513.2917 | 9600.111
2021-11-13 08:00 | 44513.3333 | 9946.084
2021-11-13 09:00 | 44513.375 | 10132.55
2021-11-13 10:00 | 44513.4167 | 10353.06
2021-11-13 11:00 | 44513.4583 | 10232.11
2021-11-13 12:00 | 44513.5 | 10107.94
2021-11-13 13:00 | 44513.5417 | 9963.568
2021-11-13 14:00 | 44513.5833 | 9937.466
2021-11-13 15:00 | 44513.625 | 9990.035
2021-11-13 16:00 | 44513.6667 | 10513.3
2021-11-13 17:00 | 44513.7083 | 10794.88
2021-11-13 18:00 | 44513.75 | 10696.35
2021-11-13 19:00 | 44513.7917 | 10360.41
2021-11-13 20:00 | 44513.8333 | 9961.79
2021-11-13 21:00 | 44513.875 | 10154.3
2021-11-13 22:00 | 44513.9167 | 10146.3
2021-11-13 23:00 | 44513.9583 | 9630.622
2021-11-14 | 44514 | 8927.128
2021-11-14 01:00 | 44514.0417 | 8470.379
2021-11-14 02:00 | 44514.0833 | 8159.555
2021-11-14 03:00 | 44514.125 | 7968.603
2021-11-14 04:00 | 44514.1667 | 7833.677
2021-11-14 05:00 | 44514.2083 | 8008.671
2021-11-14 06:00 | 44514.25 | 8389.183
2021-11-14 07:00 | 44514.2917 | 8887.879
2021-11-14 08:00 | 44514.3333 | 9400.695
2021-11-14 09:00 | 44514.375 | 9695.559
2021-11-14 10:00 | 44514.4167 | 10018.54
2021-11-14 11:00 | 44514.4583 | 9861.245
2021-11-14 12:00 | 44514.5 | 9636.77
2021-11-14 13:00 | 44514.5417 | 9427.575
2021-11-14 14:00 | 44514.5833 | 9382.091
2021-11-14 15:00 | 44514.625 | 9462.687
2021-11-14 16:00 | 44514.6667 | 10106.1
2021-11-14 17:00 | 44514.7083 | 10540.18
2021-11-14 18:00 | 44514.75 | 10534.68
2021-11-14 19:00 | 44514.7917 | 10261.88
2021-11-14 20:00 | 44514.8333 | 9842.531
2021-11-14 21:00 | 44514.875 | 10039.34
2021-11-14 22:00 | 44514.9167 | 9988.237
2021-11-14 23:00 | 44514.9583 | 9376.912
2021-11-15 | 44515 | 9467.148
2021-11-15 01:00 | 44515.0417 | 9073.642
2021-11-15 02:00 | 44515.0833 | 8907.769
2021-11-15 03:00 | 44515.125 | 8934.474
2021-11-15 04:00 | 44515.1667 | 9421.422
2021-11-15 05:00 | 44515.2083 | 10466.26
2021-11-15 06:00 | 44515.25 | 11217.15
2021-11-15 07:00 | 44515.2917 | 11527.1
2021-11-15 08:00 | 44515.3333 | 11746.64
2021-11-15 09:00 | 44515.375 | 11849.02
2021-11-15 10:00 | 44515.4167 | 11929.41
2021-11-15 11:00 | 44515.4583 | 11786.91
2021-11-15 12:00 | 44515.5 | 11767.19
2021-11-15 13:00 | 44515.5417 | 11657.68
2021-11-15 14:00 | 44515.5833 | 11634.55
2021-11-15 15:00 | 44515.625 | 11673.46
2021-11-15 16:00 | 44515.6667 | 12204.2
2021-11-15 17:00 | 44515.7083 | 12318.36
2021-11-15 18:00 | 44515.75 | 11919.59
2021-11-15 19:00 | 44515.7917 | 11292.47
2021-11-15 20:00 | 44515.8333 | 10776.16
2021-11-15 21:00 | 44515.875 | 10962.49
2021-11-15 22:00 | 44515.9167 | 10856.75
2021-11-15 23:00 | 44515.9583 | 10159.69
2021-11-16 | 44516 | 9535.795
2021-11-16 01:00 | 44516.0417 | 9145.534
2021-11-16 02:00 | 44516.0833 | 8980.196
2021-11-16 03:00 | 44516.125 | 9003.518
2021-11-16 04:00 | 44516.1667 | 9480.608
2021-11-16 05:00 | 44516.2083 | 10512.53
2021-11-16 06:00 | 44516.25 | 11254.54
2021-11-16 07:00 | 44516.2917 | 11559.39
2021-11-16 08:00 | 44516.3333 | 11776.22
2021-11-16 09:00 | 44516.375 | 11876.38
2021-11-16 10:00 | 44516.4167 | 11958.05
2021-11-16 11:00 | 44516.4583 | 11817.83
2021-11-16 12:00 | 44516.5 | 11799.5
2021-11-16 13:00 | 44516.5417 | 11692.53
2021-11-16 14:00 | 44516.5833 | 11670.17
2021-11-16 15:00 | 44516.625 | 11708.14
2021-11-16 16:00 | 44516.6667 | 12236.08
2021-11-16 17:00 | 44516.7083 | 12350.45
2021-11-16 18:00 | 44516.75 | 11955.07
2021-11-16 19:00 | 44516.7917 | 11333.07
2021-11-16 20:00 | 44516.8333 | 10818.39
2021-11-16 21:00 | 44516.875 | 11007.19
2021-11-16 22:00 | 44516.9167 | 10909.22
2021-11-16 23:00 | 44516.9583 | 10221.11
2021-11-17 | 44517 | 9582.462
2021-11-17 01:00 | 44517.0417 | 9191.918
2021-11-17 02:00 | 44517.0833 | 9026.409
2021-11-17 03:00 | 44517.125 | 9045.58
2021-11-17 04:00 | 44517.1667 | 9524.323
2021-11-17 05:00 | 44517.2083 | 10551.66
2021-11-17 06:00 | 44517.25 | 11291.91
2021-11-17 07:00 | 44517.2917 | 11599.3
2021-11-17 08:00 | 44517.3333 | 11818.52
2021-11-17 09:00 | 44517.375 | 11920.72
2021-11-17 10:00 | 44517.4167 | 12003.55
2021-11-17 11:00 | 44517.4583 | 11862.76
2021-11-17 12:00 | 44517.5 | 11842.36
2021-11-17 13:00 | 44517.5417 | 11732.63
2021-11-17 14:00 | 44517.5833 | 11709.91
2021-11-17 15:00 | 44517.625 | 11748.66
2021-11-17 16:00 | 44517.6667 | 12276.43
2021-11-17 17:00 | 44517.7083 | 12392.29
2021-11-17 18:00 | 44517.75 | 12000.34
2021-11-17 19:00 | 44517.7917 | 11381.29
2021-11-17 20:00 | 44517.8333 | 10869.1
2021-11-17 21:00 | 44517.875 | 11055.75
2021-11-17 22:00 | 44517.9167 | 10954.63
2021-11-17 23:00 | 44517.9583 | 10265.97
2021-11-18 | 44518 | 9568.927
2021-11-18 01:00 | 44518.0417 | 9176.215
2021-11-18 02:00 | 44518.0833 | 9009.554
2021-11-18 03:00 | 44518.125 | 9031.016
2021-11-18 04:00 | 44518.1667 | 9511.32
2021-11-18 05:00 | 44518.2083 | 10546.86
2021-11-18 06:00 | 44518.25 | 11292.37
2021-11-18 07:00 | 44518.2917 | 11600.24
2021-11-18 08:00 | 44518.3333 | 11819.49
2021-11-18 09:00 | 44518.375 | 11921.06
2021-11-18 10:00 | 44518.4167 | 12004.31
2021-11-18 11:00 | 44518.4583 | 11863.07
2021-11-18 12:00 | 44518.5 | 11843.64
2021-11-18 13:00 | 44518.5417 | 11734.7
2021-11-18 14:00 | 44518.5833 | 11711.97
2021-11-18 15:00 | 44518.625 | 11750.41
2021-11-18 16:00 | 44518.6667 | 12281.76
2021-11-18 17:00 | 44518.7083 | 12398.01
2021-11-18 18:00 | 44518.75 | 12001.69
2021-11-18 19:00 | 44518.7917 | 11377.32
2021-11-18 20:00 | 44518.8333 | 10860.5
2021-11-18 21:00 | 44518.875 | 11049.57
2021-11-18 22:00 | 44518.9167 | 10949.72
2021-11-18 23:00 | 44518.9583 | 10257.14
2021-11-19 | 44519 | 9544.1
2021-11-19 01:00 | 44519.0417 | 9147.314
2021-11-19 02:00 | 44519.0833 | 8978.371
2021-11-19 03:00 | 44519.125 | 8997.539
2021-11-19 04:00 | 44519.1667 | 9490.154
2021-11-19 05:00 | 44519.2083 | 10545.91
2021-11-19 06:00 | 44519.25 | 11303.38
2021-11-19 07:00 | 44519.2917 | 11610.09
2021-11-19 08:00 | 44519.3333 | 11827.58
2021-11-19 09:00 | 44519.375 | 11926.71
2021-11-19 10:00 | 44519.4167 | 12009.98
2021-11-19 11:00 | 44519.4583 | 11868.4
2021-11-19 12:00 | 44519.5 | 11852.77
2021-11-19 13:00 | 44519.5417 | 11744.96
2021-11-19 14:00 | 44519.5833 | 11722.78
2021-11-19 15:00 | 44519.625 | 11760.62
2021-11-19 16:00 | 44519.6667 | 12299.78
2021-11-19 17:00 | 44519.7083 | 12415.51
2021-11-19 18:00 | 44519.75 | 12007.46
2021-11-19 19:00 | 44519.7917 | 11369.9
2021-11-19 20:00 | 44519.8333 | 10841.69
2021-11-19 21:00 | 44519.875 | 11037.3
2021-11-19 22:00 | 44519.9167 | 10942.51
2021-11-19 23:00 | 44519.9583 | 10242.55
2021-11-20 | 44520 | 9297.693
2021-11-20 01:00 | 44520.0417 | 8923.144
2021-11-20 02:00 | 44520.0833 | 8673.53
2021-11-20 03:00 | 44520.125 | 8573.734
2021-11-20 04:00 | 44520.1667 | 8559.593
2021-11-20 05:00 | 44520.2083 | 8935.249
2021-11-20 06:00 | 44520.25 | 9354.461
2021-11-20 07:00 | 44520.2917 | 9686.749
2021-11-20 08:00 | 44520.3333 | 10020.87
2021-11-20 09:00 | 44520.375 | 10193.78
2021-11-20 10:00 | 44520.4167 | 10423.01
2021-11-20 11:00 | 44520.4583 | 10308.38
2021-11-20 12:00 | 44520.5 | 10199.84
2021-11-20 13:00 | 44520.5417 | 10060.46
2021-11-20 14:00 | 44520.5833 | 10039.14
2021-11-20 15:00 | 44520.625 | 10087.98
2021-11-20 16:00 | 44520.6667 | 10631.32
2021-11-20 17:00 | 44520.7083 | 10914.96
2021-11-20 18:00 | 44520.75 | 10790.7
2021-11-20 19:00 | 44520.7917 | 10428.78
2021-11-20 20:00 | 44520.8333 | 9997.134
2021-11-20 21:00 | 44520.875 | 10219.65
2021-11-20 22:00 | 44520.9167 | 10253.55
2021-11-20 23:00 | 44520.9583 | 9741.305
2021-11-21 | 44521 | 8987.563
2021-11-21 01:00 | 44521.0417 | 8527.541
2021-11-21 02:00 | 44521.0833 | 8211.445
2021-11-21 03:00 | 44521.125 | 8010.292
2021-11-21 04:00 | 44521.1667 | 7875.483
2021-11-21 05:00 | 44521.2083 | 8063.13
2021-11-21 06:00 | 44521.25 | 8458.416
2021-11-21 07:00 | 44521.2917 | 8942.139
2021-11-21 08:00 | 44521.3333 | 9444.647
2021-11-21 09:00 | 44521.375 | 9728.043
2021-11-21 10:00 | 44521.4167 | 10057.74
2021-11-21 11:00 | 44521.4583 | 9905.557
2021-11-21 12:00 | 44521.5 | 9693.975
2021-11-21 13:00 | 44521.5417 | 9488.966
2021-11-21 14:00 | 44521.5833 | 9447.324
2021-11-21 15:00 | 44521.625 | 9524.735
2021-11-21 16:00 | 44521.6667 | 10183.73
2021-11-21 17:00 | 44521.7083 | 10616.17
2021-11-21 18:00 | 44521.75 | 10601
2021-11-21 19:00 | 44521.7917 | 10297.35
2021-11-21 20:00 | 44521.8333 | 9851.671
2021-11-21 21:00 | 44521.875 | 10072.18
2021-11-21 22:00 | 44521.9167 | 10054.05
2021-11-21 23:00 | 44521.9583 | 9445.232
2021-11-22 | 44522 | 9519.076
2021-11-22 01:00 | 44522.0417 | 9124.276
2021-11-22 02:00 | 44522.0833 | 8956.001
2021-11-22 03:00 | 44522.125 | 8979.543
2021-11-22 04:00 | 44522.1667 | 9459.871
2021-11-22 05:00 | 44522.2083 | 10505.07
2021-11-22 06:00 | 44522.25 | 11256.16
2021-11-22 07:00 | 44522.2917 | 11562.05
2021-11-22 08:00 | 44522.3333 | 11779.58
2021-11-22 09:00 | 44522.375 | 11878.89
2021-11-22 10:00 | 44522.4167 | 11963.77
2021-11-22 11:00 | 44522.4583 | 11823.16
2021-11-22 12:00 | 44522.5 | 11806.61
2021-11-22 13:00 | 44522.5417 | 11697.72
2021-11-22 14:00 | 44522.5833 | 11675.63
2021-11-22 15:00 | 44522.625 | 11713.55
2021-11-22 16:00 | 44522.6667 | 12250.13
2021-11-22 17:00 | 44522.7083 | 12366.57
2021-11-22 18:00 | 44522.75 | 11963.33
2021-11-22 19:00 | 44522.7917 | 11331.39
2021-11-22 20:00 | 44522.8333 | 10806.97
2021-11-22 21:00 | 44522.875 | 11001.41
2021-11-22 22:00 | 44522.9167 | 10907.41
2021-11-22 23:00 | 44522.9583 | 10212.15
2021-11-23 | 44523 | 9551.76
2021-11-23 01:00 | 44523.0417 | 9157.193
2021-11-23 02:00 | 44523.0833 | 8988.701
2021-11-23 03:00 | 44523.125 | 9010.453
2021-11-23 04:00 | 44523.1667 | 9493.553
2021-11-23 05:00 | 44523.2083 | 10543.92
2021-11-23 06:00 | 44523.25 | 11296.86
2021-11-23 07:00 | 44523.2917 | 11598.81
2021-11-23 08:00 | 44523.3333 | 11813.05
2021-11-23 09:00 | 44523.375 | 11909.53
2021-11-23 10:00 | 44523.4167 | 11993.93
2021-11-23 11:00 | 44523.4583 | 11854.46
2021-11-23 12:00 | 44523.5 | 11841.19
2021-11-23 13:00 | 44523.5417 | 11734.15
2021-11-23 14:00 | 44523.5833 | 11712.9
2021-11-23 15:00 | 44523.625 | 11749.95
2021-11-23 16:00 | 44523.6667 | 12288
2021-11-23 17:00 | 44523.7083 | 12403.06
2021-11-23 18:00 | 44523.75 | 11994.97
2021-11-23 19:00 | 44523.7917 | 11358.74
2021-11-23 20:00 | 44523.8333 | 10829.93
2021-11-23 21:00 | 44523.875 | 11028.38
2021-11-23 22:00 | 44523.9167 | 10940.39
2021-11-23 23:00 | 44523.9583 | 10246.38
2021-11-24 | 44524 | 9616.229
2021-11-24 01:00 | 44524.0417 | 9224.478
2021-11-24 02:00 | 44524.0833 | 9057.079
2021-11-24 03:00 | 44524.125 | 9077.164
2021-11-24 04:00 | 44524.1667 | 9549.726
2021-11-24 05:00 | 44524.2083 | 10581.18
2021-11-24 06:00 | 44524.25 | 11323.45
2021-11-24 07:00 | 44524.2917 | 11626.6
2021-11-24 08:00 | 44524.3333 | 11843.12
2021-11-24 09:00 | 44524.375 | 11942
2021-11-24 10:00 | 44524.4167 | 12027.46
2021-11-24 11:00 | 44524.4583 | 11888.33
2021-11-24 12:00 | 44524.5 | 11871.54
2021-11-24 13:00 | 44524.5417 | 11763.84
2021-11-24 14:00 | 44524.5833 | 11742.13
2021-11-24 15:00 | 44524.625 | 11779.59
2021-11-24 16:00 | 44524.6667 | 12312.46
2021-11-24 17:00 | 44524.7083 | 12429.34
2021-11-24 18:00 | 44524.75 | 12031.56
2021-11-24 19:00 | 44524.7917 | 11406.49
2021-11-24 20:00 | 44524.8333 | 10886.19
2021-11-24 21:00 | 44524.875 | 11080.4
2021-11-24 22:00 | 44524.9167 | 10989.87
2021-11-24 23:00 | 44524.9583 | 10302.16
2021-11-25 | 44525 | 9635.116
2021-11-25 01:00 | 44525.0417 | 9241.955
2021-11-25 02:00 | 44525.0833 | 9072.161
2021-11-25 03:00 | 44525.125 | 9092.405
2021-11-25 04:00 | 44525.1667 | 9560.065
2021-11-25 05:00 | 44525.2083 | 10598.78
2021-11-25 06:00 | 44525.25 | 11344.37
2021-11-25 07:00 | 44525.2917 | 11641.33
2021-11-25 08:00 | 44525.3333 | 11853.82
2021-11-25 09:00 | 44525.375 | 11948.2
2021-11-25 10:00 | 44525.4167 | 12036.17
2021-11-25 11:00 | 44525.4583 | 11899.05
2021-11-25 12:00 | 44525.5 | 11887.49
2021-11-25 13:00 | 44525.5417 | 11781.52
2021-11-25 14:00 | 44525.5833 | 11761.43
2021-11-25 15:00 | 44525.625 | 11797.69
2021-11-25 16:00 | 44525.6667 | 12337.08
2021-11-25 17:00 | 44525.7083 | 12454.44
2021-11-25 18:00 | 44525.75 | 12047.94
2021-11-25 19:00 | 44525.7917 | 11414.14
2021-11-25 20:00 | 44525.8333 | 10882.91
2021-11-25 21:00 | 44525.875 | 11087.04
2021-11-25 22:00 | 44525.9167 | 11010.35
2021-11-25 23:00 | 44525.9583 | 10323.79
2021-11-26 | 44526 | 9671.641
2021-11-26 01:00 | 44526.0417 | 9281.54
2021-11-26 02:00 | 44526.0833 | 9114.72
2021-11-26 03:00 | 44526.125 | 9133.152
2021-11-26 04:00 | 44526.1667 | 9605.267
2021-11-26 05:00 | 44526.2083 | 10633.83
2021-11-26 06:00 | 44526.25 | 11373.41
2021-11-26 07:00 | 44526.2917 | 11674.03
2021-11-26 08:00 | 44526.3333 | 11888.47
2021-11-26 09:00 | 44526.375 | 11985.6
2021-11-26 10:00 | 44526.4167 | 12071.22
2021-11-26 11:00 | 44526.4583 | 11933.07
2021-11-26 12:00 | 44526.5 | 11917.34
2021-11-26 13:00 | 44526.5417 | 11810.68
2021-11-26 14:00 | 44526.5833 | 11789.24
2021-11-26 15:00 | 44526.625 | 11826.16
2021-11-26 16:00 | 44526.6667 | 12357.1
2021-11-26 17:00 | 44526.7083 | 12472.97
2021-11-26 18:00 | 44526.75 | 12075.58
2021-11-26 19:00 | 44526.7917 | 11451.9
2021-11-26 20:00 | 44526.8333 | 10932.47
2021-11-26 21:00 | 44526.875 | 11127.18
2021-11-26 22:00 | 44526.9167 | 11039.01
2021-11-26 23:00 | 44526.9583 | 10354.7
2021-11-27 | 44527 | 9389.247
2021-11-27 01:00 | 44527.0417 | 9017.904
2021-11-27 02:00 | 44527.0833 | 8771.057
2021-11-27 03:00 | 44527.125 | 8670.184
2021-11-27 04:00 | 44527.1667 | 8661.482
2021-11-27 05:00 | 44527.2083 | 9033.28
2021-11-27 06:00 | 44527.25 | 9449.235
2021-11-27 07:00 | 44527.2917 | 9779.596
2021-11-27 08:00 | 44527.3333 | 10110.87
2021-11-27 09:00 | 44527.375 | 10282.32
2021-11-27 10:00 | 44527.4167 | 10509.98
2021-11-27 11:00 | 44527.4583 | 10396.22
2021-11-27 12:00 | 44527.5 | 10288.13
2021-11-27 13:00 | 44527.5417 | 10148.75
2021-11-27 14:00 | 44527.5833 | 10127.41
2021-11-27 15:00 | 44527.625 | 10175.85
2021-11-27 16:00 | 44527.6667 | 10713.57
2021-11-27 17:00 | 44527.7083 | 10994.01
2021-11-27 18:00 | 44527.75 | 10871.8
2021-11-27 19:00 | 44527.7917 | 10513.67
2021-11-27 20:00 | 44527.8333 | 10087.22
2021-11-27 21:00 | 44527.875 | 10306.34
2021-11-27 22:00 | 44527.9167 | 10337.67
2021-11-27 23:00 | 44527.9583 | 9829.345
2021-11-28 | 44528 | 9063.222
2021-11-28 01:00 | 44528.0417 | 8602.465
2021-11-28 02:00 | 44528.0833 | 8287.267
2021-11-28 03:00 | 44528.125 | 8089.605
2021-11-28 04:00 | 44528.1667 | 7972.516
2021-11-28 05:00 | 44528.2083 | 8181.999
2021-11-28 06:00 | 44528.25 | 8592.584
2021-11-28 07:00 | 44528.2917 | 9072.149
2021-11-28 08:00 | 44528.3333 | 9568.143
2021-11-28 09:00 | 44528.375 | 9846.4
2021-11-28 10:00 | 44528.4167 | 10172.07
2021-11-28 11:00 | 44528.4583 | 10020.15
2021-11-28 12:00 | 44528.5 | 9814.247
2021-11-28 13:00 | 44528.5417 | 9612.63
2021-11-28 14:00 | 44528.5833 | 9571.431
2021-11-28 15:00 | 44528.625 | 9647.364
2021-11-28 16:00 | 44528.6667 | 10307.85
2021-11-28 17:00 | 44528.7083 | 10734.21
2021-11-28 18:00 | 44528.75 | 10708.88
2021-11-28 19:00 | 44528.7917 | 10389.74
2021-11-28 20:00 | 44528.8333 | 9936.738
2021-11-28 21:00 | 44528.875 | 10160.37
2021-11-28 22:00 | 44528.9167 | 10143.98
2021-11-28 23:00 | 44528.9583 | 9530.251
2021-11-29 | 44529 | 9692.086
2021-11-29 01:00 | 44529.0417 | 9301.554
2021-11-29 02:00 | 44529.0833 | 9134.243
2021-11-29 03:00 | 44529.125 | 9151.25
2021-11-29 04:00 | 44529.1667 | 9627.022
2021-11-29 05:00 | 44529.2083 | 10663.38
2021-11-29 06:00 | 44529.25 | 11406.49
2021-11-29 07:00 | 44529.2917 | 11703.34
2021-11-29 08:00 | 44529.3333 | 11914.49
2021-11-29 09:00 | 44529.375 | 12008.62
2021-11-29 10:00 | 44529.4167 | 12094.26
2021-11-29 11:00 | 44529.4583 | 11957.2
2021-11-29 12:00 | 44529.5 | 11945.02
2021-11-29 13:00 | 44529.5417 | 11839.43
2021-11-29 14:00 | 44529.5833 | 11818.9
2021-11-29 15:00 | 44529.625 | 11855.02
2021-11-29 16:00 | 44529.6667 | 12388.73
2021-11-29 17:00 | 44529.7083 | 12503.34
2021-11-29 18:00 | 44529.75 | 12099.73
2021-11-29 19:00 | 44529.7917 | 11470.13
2021-11-29 20:00 | 44529.8333 | 10944.92
2021-11-29 21:00 | 44529.875 | 11144.38
2021-11-29 22:00 | 44529.9167 | 11062.57
2021-11-29 23:00 | 44529.9583 | 10378.27
2021-11-30 | 44530 | 9660.516
2021-11-30 01:00 | 44530.0417 | 9262.054
2021-11-30 02:00 | 44530.0833 | 9088.285
2021-11-30 03:00 | 44530.125 | 9104.911
2021-11-30 04:00 | 44530.1667 | 9577
2021-11-30 05:00 | 44530.2083 | 10630.44
2021-11-30 06:00 | 44530.25 | 11385.98
2021-11-30 07:00 | 44530.2917 | 11682.5
2021-11-30 08:00 | 44530.3333 | 11895.16
2021-11-30 09:00 | 44530.375 | 11987.59
2021-11-30 10:00 | 44530.4167 | 12079.01
2021-11-30 11:00 | 44530.4583 | 11941.83
2021-11-30 12:00 | 44530.5 | 11933.29
2021-11-30 13:00 | 44530.5417 | 11828.34
2021-11-30 14:00 | 44530.5833 | 11808.76
2021-11-30 15:00 | 44530.625 | 11844.34
2021-11-30 16:00 | 44530.6667 | 12394.33
2021-11-30 17:00 | 44530.7083 | 12514.31
2021-11-30 18:00 | 44530.75 | 12097.64
2021-11-30 19:00 | 44530.7917 | 11451.39
2021-11-30 20:00 | 44530.8333 | 10906.85
2021-11-30 21:00 | 44530.875 | 11119.83
2021-11-30 22:00 | 44530.9167 | 11051.49
2021-11-30 23:00 | 44530.9583 | 10357.92
2021-12-01 | 44531 | 9641.952
2021-12-01 01:00 | 44531.0417 | 9245.142
2021-12-01 02:00 | 44531.0833 | 9073.599
2021-12-01 03:00 | 44531.125 | 9090.184
2021-12-01 04:00 | 44531.1667 | 9567.26
2021-12-01 05:00 | 44531.2083 | 10617.39
2021-12-01 06:00 | 44531.25 | 11370.9
2021-12-01 07:00 | 44531.2917 | 11670.15
2021-12-01 08:00 | 44531.3333 | 11884
2021-12-01 09:00 | 44531.375 | 11978.47
2021-12-01 10:00 | 44531.4167 | 12068.29
2021-12-01 11:00 | 44531.4583 | 11930.42
2021-12-01 12:00 | 44531.5 | 11919.47
2021-12-01 13:00 | 44531.5417 | 11811.27
2021-12-01 14:00 | 44531.5833 | 11791.1
2021-12-01 15:00 | 44531.625 | 11827.71
2021-12-01 16:00 | 44531.6667 | 12373.09
2021-12-01 17:00 | 44531.7083 | 12491.69
2021-12-01 18:00 | 44531.75 | 12079.76
2021-12-01 19:00 | 44531.7917 | 11438.77
2021-12-01 20:00 | 44531.8333 | 10901.45
2021-12-01 21:00 | 44531.875 | 11108.07
2021-12-01 22:00 | 44531.9167 | 11031.25
2021-12-01 23:00 | 44531.9583 | 10337.77
2021-12-02 | 44532 | 9670.439
2021-12-02 01:00 | 44532.0417 | 9272.324
2021-12-02 02:00 | 44532.0833 | 9099.247
2021-12-02 03:00 | 44532.125 | 9111.593
2021-12-02 04:00 | 44532.1667 | 9586.233
2021-12-02 05:00 | 44532.2083 | 10633.5
2021-12-02 06:00 | 44532.25 | 11386.28
2021-12-02 07:00 | 44532.2917 | 11685.95
2021-12-02 08:00 | 44532.3333 | 11901.3
2021-12-02 09:00 | 44532.375 | 11996.36
2021-12-02 10:00 | 44532.4167 | 12088.03
2021-12-02 11:00 | 44532.4583 | 11950.24
2021-12-02 12:00 | 44532.5 | 11938.96
2021-12-02 13:00 | 44532.5417 | 11831.65
2021-12-02 14:00 | 44532.5833 | 11811.51
2021-12-02 15:00 | 44532.625 | 11847.96
2021-12-02 16:00 | 44532.6667 | 12396.07
2021-12-02 17:00 | 44532.7083 | 12517.25
2021-12-02 18:00 | 44532.75 | 12105.71
2021-12-02 19:00 | 44532.7917 | 11464.33
2021-12-02 20:00 | 44532.8333 | 10924.55
2021-12-02 21:00 | 44532.875 | 11133.71
2021-12-02 22:00 | 44532.9167 | 11060.21
2021-12-02 23:00 | 44532.9583 | 10366.63
2021-12-03 | 44533 | 9692.457
2021-12-03 01:00 | 44533.0417 | 9294.755
2021-12-03 02:00 | 44533.0833 | 9120.67
2021-12-03 03:00 | 44533.125 | 9132.673
2021-12-03 04:00 | 44533.1667 | 9597.515
2021-12-03 05:00 | 44533.2083 | 10638.83
2021-12-03 06:00 | 44533.25 | 11387.97
2021-12-03 07:00 | 44533.2917 | 11684.8
2021-12-03 08:00 | 44533.3333 | 11899.24
2021-12-03 09:00 | 44533.375 | 11992.76
2021-12-03 10:00 | 44533.4167 | 12087.2
2021-12-03 11:00 | 44533.4583 | 11950.82
2021-12-03 12:00 | 44533.5 | 11940.76
2021-12-03 13:00 | 44533.5417 | 11833.58
2021-12-03 14:00 | 44533.5833 | 11814.17
2021-12-03 15:00 | 44533.625 | 11850.19
2021-12-03 16:00 | 44533.6667 | 12399.93
2021-12-03 17:00 | 44533.7083 | 12522.72
2021-12-03 18:00 | 44533.75 | 12111.48
2021-12-03 19:00 | 44533.7917 | 11470.68
2021-12-03 20:00 | 44533.8333 | 10928.56
2021-12-03 21:00 | 44533.875 | 11141.59
2021-12-03 22:00 | 44533.9167 | 11075.14
2021-12-03 23:00 | 44533.9583 | 10385.33
2021-12-04 | 44534 | 9439.687
2021-12-04 01:00 | 44534.0417 | 9067.707
2021-12-04 02:00 | 44534.0833 | 8818.96
2021-12-04 03:00 | 44534.125 | 8717.879
2021-12-04 04:00 | 44534.1667 | 8705.63
2021-12-04 05:00 | 44534.2083 | 9082.647
2021-12-04 06:00 | 44534.25 | 9500.672
2021-12-04 07:00 | 44534.2917 | 9825.203
2021-12-04 08:00 | 44534.3333 | 10152.4
2021-12-04 09:00 | 44534.375 | 10319.37
2021-12-04 10:00 | 44534.4167 | 10549.16
2021-12-04 11:00 | 44534.4583 | 10437.54
2021-12-04 12:00 | 44534.5 | 10334.2
2021-12-04 13:00 | 44534.5417 | 10196.9
2021-12-04 14:00 | 44534.5833 | 10176.92
2021-12-04 15:00 | 44534.625 | 10224.06
2021-12-04 16:00 | 44534.6667 | 10766.4
2021-12-04 17:00 | 44534.7083 | 11046.85
2021-12-04 18:00 | 44534.75 | 10917.55
2021-12-04 19:00 | 44534.7917 | 10552.61
2021-12-04 20:00 | 44534.8333 | 10117.5
2021-12-04 21:00 | 44534.875 | 10344.84
2021-12-04 22:00 | 44534.9167 | 10388.07
2021-12-04 23:00 | 44534.9583 | 9881.583
2021-12-05 | 44535 | 9134.302
2021-12-05 01:00 | 44535.0417 | 8670.101
2021-12-05 02:00 | 44535.0833 | 8353.213
2021-12-05 03:00 | 44535.125 | 8153.86
2021-12-05 04:00 | 44535.1667 | 8034.07
2021-12-05 05:00 | 44535.2083 | 8236.537
2021-12-05 06:00 | 44535.25 | 8646.25
2021-12-05 07:00 | 44535.2917 | 9135.868
2021-12-05 08:00 | 44535.3333 | 9640.874
2021-12-05 09:00 | 44535.375 | 9925.696
2021-12-05 10:00 | 44535.4167 | 10254.26
2021-12-05 11:00 | 44535.4583 | 10099.67
2021-12-05 12:00 | 44535.5 | 9887.074
2021-12-05 13:00 | 44535.5417 | 9681.456
2021-12-05 14:00 | 44535.5833 | 9638.503
2021-12-05 15:00 | 44535.625 | 9716.223
2021-12-05 16:00 | 44535.6667 | 10378.81
2021-12-05 17:00 | 44535.7083 | 10810.9
2021-12-05 18:00 | 44535.75 | 10794.37
2021-12-05 19:00 | 44535.7917 | 10479.48
2021-12-05 20:00 | 44535.8333 | 10030.73
2021-12-05 21:00 | 44535.875 | 10249.1
2021-12-05 22:00 | 44535.9167 | 10222.46
2021-12-05 23:00 | 44535.9583 | 9602.407
2021-12-06 | 44536 | 9797.999
2021-12-06 01:00 | 44536.0417 | 9406.683
2021-12-06 02:00 | 44536.0833 | 9236.313
2021-12-06 03:00 | 44536.125 | 9247.779
2021-12-06 04:00 | 44536.1667 | 9708.706
2021-12-06 05:00 | 44536.2083 | 10736.01
2021-12-06 06:00 | 44536.25 | 11474.21
2021-12-06 07:00 | 44536.2917 | 11766.26
2021-12-06 08:00 | 44536.3333 | 11976.54
2021-12-06 09:00 | 44536.375 | 12068.12
2021-12-06 10:00 | 44536.4167 | 12159.3
2021-12-06 11:00 | 44536.4583 | 12024.71
2021-12-06 12:00 | 44536.5 | 12014.99
2021-12-06 13:00 | 44536.5417 | 11911.65
2021-12-06 14:00 | 44536.5833 | 11892.37
2021-12-06 15:00 | 44536.625 | 11927.33
2021-12-06 16:00 | 44536.6667 | 12466.69
2021-12-06 17:00 | 44536.7083 | 12585.78
2021-12-06 18:00 | 44536.75 | 12181.15
2021-12-06 19:00 | 44536.7917 | 11550.23
2021-12-06 20:00 | 44536.8333 | 11017.51
2021-12-06 21:00 | 44536.875 | 11226.37
2021-12-06 22:00 | 44536.9167 | 11159.79
2021-12-06 23:00 | 44536.9583 | 10480.79
2021-12-07 | 44537 | 9769.35
2021-12-07 01:00 | 44537.0417 | 9372.611
2021-12-07 02:00 | 44537.0833 | 9198.454
2021-12-07 03:00 | 44537.125 | 9210.403
2021-12-07 04:00 | 44537.1667 | 9671.093
2021-12-07 05:00 | 44537.2083 | 10709.81
2021-12-07 06:00 | 44537.25 | 11456.74
2021-12-07 07:00 | 44537.2917 | 11750.89
2021-12-07 08:00 | 44537.3333 | 11963.62
2021-12-07 09:00 | 44537.375 | 12055.66
2021-12-07 10:00 | 44537.4167 | 12150.53
2021-12-07 11:00 | 44537.4583 | 12015.27
2021-12-07 12:00 | 44537.5 | 12006.59
2021-12-07 13:00 | 44537.5417 | 11900.54
2021-12-07 14:00 | 44537.5833 | 11881.64
2021-12-07 15:00 | 44537.625 | 11917.05
2021-12-07 16:00 | 44537.6667 | 12466.5
2021-12-07 17:00 | 44537.7083 | 12589.1
2021-12-07 18:00 | 44537.75 | 12177.43
2021-12-07 19:00 | 44537.7917 | 11536.86
2021-12-07 20:00 | 44537.8333 | 10993.76
2021-12-07 21:00 | 44537.875 | 11208.84
2021-12-07 22:00 | 44537.9167 | 11146.69
2021-12-07 23:00 | 44537.9583 | 10459.92
2021-12-08 | 44538 | 9748.294
2021-12-08 01:00 | 44538.0417 | 9349.271
2021-12-08 02:00 | 44538.0833 | 9174.401
2021-12-08 03:00 | 44538.125 | 9190.594
2021-12-08 04:00 | 44538.1667 | 9655.66
2021-12-08 05:00 | 44538.2083 | 10706.17
2021-12-08 06:00 | 44538.25 | 11460.3
2021-12-08 07:00 | 44538.2917 | 11755.46
2021-12-08 08:00 | 44538.3333 | 11968.08
2021-12-08 09:00 | 44538.375 | 12059.53
2021-12-08 10:00 | 44538.4167 | 12153.91
2021-12-08 11:00 | 44538.4583 | 12017.92
2021-12-08 12:00 | 44538.5 | 12010.35
2021-12-08 13:00 | 44538.5417 | 11904.55
2021-12-08 14:00 | 44538.5833 | 11885.52
2021-12-08 15:00 | 44538.625 | 11920.93
2021-12-08 16:00 | 44538.6667 | 12473.55
2021-12-08 17:00 | 44538.7083 | 12595.54
2021-12-08 18:00 | 44538.75 | 12178.44
2021-12-08 19:00 | 44538.7917 | 11531.51
2021-12-08 20:00 | 44538.8333 | 10984.02
2021-12-08 21:00 | 44538.875 | 11200.52
2021-12-08 22:00 | 44538.9167 | 11137.6
2021-12-08 23:00 | 44538.9583 | 10445.51
2021-12-09 | 44539 | 9752.938
2021-12-09 01:00 | 44539.0417 | 9353.618
2021-12-09 02:00 | 44539.0833 | 9178.04
2021-12-09 03:00 | 44539.125 | 9192.691
2021-12-09 04:00 | 44539.1667 | 9659.345
2021-12-09 05:00 | 44539.2083 | 10715.56
2021-12-09 06:00 | 44539.25 | 11472.08
2021-12-09 07:00 | 44539.2917 | 11763.34
2021-12-09 08:00 | 44539.3333 | 11972.89
2021-12-09 09:00 | 44539.375 | 12061.24
2021-12-09 10:00 | 44539.4167 | 12156.21
2021-12-09 11:00 | 44539.4583 | 12021.37
2021-12-09 12:00 | 44539.5 | 12017.21
2021-12-09 13:00 | 44539.5417 | 11912.72
2021-12-09 14:00 | 44539.5833 | 11894.64
2021-12-09 15:00 | 44539.625 | 11929.18
2021-12-09 16:00 | 44539.6667 | 12484.46
2021-12-09 17:00 | 44539.7083 | 12605.61
2021-12-09 18:00 | 44539.75 | 12183.05
2021-12-09 19:00 | 44539.7917 | 11530.92
2021-12-09 20:00 | 44539.8333 | 10977.82
2021-12-09 21:00 | 44539.875 | 11199.24
2021-12-09 22:00 | 44539.9167 | 11143.3
2021-12-09 23:00 | 44539.9583 | 10451.93
2021-12-10 | 44540 | 9813.123
2021-12-10 01:00 | 44540.0417 | 9420.264
2021-12-10 02:00 | 44540.0833 | 9249.339
2021-12-10 03:00 | 44540.125 | 9263.925
2021-12-10 04:00 | 44540.1667 | 9722.494
2021-12-10 05:00 | 44540.2083 | 10749.39
2021-12-10 06:00 | 44540.25 | 11488.79
2021-12-10 07:00 | 44540.2917 | 11784.79
2021-12-10 08:00 | 44540.3333 | 11998.33
2021-12-10 09:00 | 44540.375 | 12092.55
2021-12-10 10:00 | 44540.4167 | 12184.58
2021-12-10 11:00 | 44540.4583 | 12049.02
2021-12-10 12:00 | 44540.5 | 12037.08
2021-12-10 13:00 | 44540.5417 | 11931.01
2021-12-10 14:00 | 44540.5833 | 11911.22
2021-12-10 15:00 | 44540.625 | 11947.1
2021-12-10 16:00 | 44540.6667 | 12487.7
2021-12-10 17:00 | 44540.7083 | 12608.48
2021-12-10 18:00 | 44540.75 | 12205.83
2021-12-10 19:00 | 44540.7917 | 11575.78
2021-12-10 20:00 | 44540.8333 | 11044.22
2021-12-10 21:00 | 44540.875 | 11251.01
2021-12-10 22:00 | 44540.9167 | 11179.98
2021-12-10 23:00 | 44540.9583 | 10497.65
2021-12-11 | 44541 | 9476.652
2021-12-11 01:00 | 44541.0417 | 9105.562
2021-12-11 02:00 | 44541.0833 | 8856.59
2021-12-11 03:00 | 44541.125 | 8752.829
2021-12-11 04:00 | 44541.1667 | 8742.801
2021-12-11 05:00 | 44541.2083 | 9124.212
2021-12-11 06:00 | 44541.25 | 9543.189
2021-12-11 07:00 | 44541.2917 | 9861.501
2021-12-11 08:00 | 44541.3333 | 10183.66
2021-12-11 09:00 | 44541.375 | 10346.12
2021-12-11 10:00 | 44541.4167 | 10575.74
2021-12-11 11:00 | 44541.4583 | 10466.13
2021-12-11 12:00 | 44541.5 | 10367.42
2021-12-11 13:00 | 44541.5417 | 10233.25
2021-12-11 14:00 | 44541.5833 | 10214.43
2021-12-11 15:00 | 44541.625 | 10260.11
2021-12-11 16:00 | 44541.6667 | 10803.68
2021-12-11 17:00 | 44541.7083 | 11082.27
2021-12-11 18:00 | 44541.75 | 10947.04
2021-12-11 19:00 | 44541.7917 | 10577.27
2021-12-11 20:00 | 44541.8333 | 10136.68
2021-12-11 21:00 | 44541.875 | 10369.73
2021-12-11 22:00 | 44541.9167 | 10422.21
2021-12-11 23:00 | 44541.9583 | 9918.922
2021-12-12 | 44542 | 9143.962
2021-12-12 01:00 | 44542.0417 | 8683.734
2021-12-12 02:00 | 44542.0833 | 8367.08
2021-12-12 03:00 | 44542.125 | 8163.963
2021-12-12 04:00 | 44542.1667 | 8040.426
2021-12-12 05:00 | 44542.2083 | 8245.368
2021-12-12 06:00 | 44542.25 | 8653.066
2021-12-12 07:00 | 44542.2917 | 9126.891
2021-12-12 08:00 | 44542.3333 | 9619.791
2021-12-12 09:00 | 44542.375 | 9894.564
2021-12-12 10:00 | 44542.4167 | 10223.79
2021-12-12 11:00 | 44542.4583 | 10074.83
2021-12-12 12:00 | 44542.5 | 9872.585
2021-12-12 13:00 | 44542.5417 | 9670.921
2021-12-12 14:00 | 44542.5833 | 9631.293
2021-12-12 15:00 | 44542.625 | 9706.359
2021-12-12 16:00 | 44542.6667 | 10370.09
2021-12-12 17:00 | 44542.7083 | 10797.78
2021-12-12 18:00 | 44542.75 | 10771.62
2021-12-12 19:00 | 44542.7917 | 10448.94
2021-12-12 20:00 | 44542.8333 | 9990.387
2021-12-12 21:00 | 44542.875 | 10221.26
2021-12-12 22:00 | 44542.9167 | 10217.16
2021-12-12 23:00 | 44542.9583 | 9608.682
2021-12-13 | 44543 | 9703.613
2021-12-13 01:00 | 44543.0417 | 9303.852
2021-12-13 02:00 | 44543.0833 | 9127.95
2021-12-13 03:00 | 44543.125 | 9140.601
2021-12-13 04:00 | 44543.1667 | 9613.296
2021-12-13 05:00 | 44543.2083 | 10675.67
2021-12-13 06:00 | 44543.25 | 11435.26
2021-12-13 07:00 | 44543.2917 | 11725.09
2021-12-13 08:00 | 44543.3333 | 11932.96
2021-12-13 09:00 | 44543.375 | 12020.07
2021-12-13 10:00 | 44543.4167 | 12114.41
2021-12-13 11:00 | 44543.4583 | 11979.89
2021-12-13 12:00 | 44543.5 | 11977.41
2021-12-13 13:00 | 44543.5417 | 11872.96
2021-12-13 14:00 | 44543.5833 | 11855.22
2021-12-13 15:00 | 44543.625 | 11889.6
2021-12-13 16:00 | 44543.6667 | 12446.24
2021-12-13 17:00 | 44543.7083 | 12566.27
2021-12-13 18:00 | 44543.75 | 12139.94
2021-12-13 19:00 | 44543.7917 | 11484.12
2021-12-13 20:00 | 44543.8333 | 10928.16
2021-12-13 21:00 | 44543.875 | 11151.36
2021-12-13 22:00 | 44543.9167 | 11097.2
2021-12-13 23:00 | 44543.9583 | 10404.67
2021-12-14 | 44544 | 9694.621
2021-12-14 01:00 | 44544.0417 | 9293.321
2021-12-14 02:00 | 44544.0833 | 9117.169
2021-12-14 03:00 | 44544.125 | 9130.453
2021-12-14 04:00 | 44544.1667 | 9608.402
2021-12-14 05:00 | 44544.2083 | 10678.31
2021-12-14 06:00 | 44544.25 | 11442.64
2021-12-14 07:00 | 44544.2917 | 11733.69
2021-12-14 08:00 | 44544.3333 | 11941.9
2021-12-14 09:00 | 44544.375 | 12029.07
2021-12-14 10:00 | 44544.4167 | 12123.27
2021-12-14 11:00 | 44544.4583 | 11988.19
2021-12-14 12:00 | 44544.5 | 11986.13
2021-12-14 13:00 | 44544.5417 | 11880.37
2021-12-14 14:00 | 44544.5833 | 11862.6
2021-12-14 15:00 | 44544.625 | 11897.32
2021-12-14 16:00 | 44544.6667 | 12456.21
2021-12-14 17:00 | 44544.7083 | 12575.91
2021-12-14 18:00 | 44544.75 | 12146.46
2021-12-14 19:00 | 44544.7917 | 11486.81
2021-12-14 20:00 | 44544.8333 | 10928.46
2021-12-14 21:00 | 44544.875 | 11151.97
2021-12-14 22:00 | 44544.9167 | 11096.32
2021-12-14 23:00 | 44544.9583 | 10399.93
2021-12-15 | 44545 | 9678.225
2021-12-15 01:00 | 44545.0417 | 9275.611
2021-12-15 02:00 | 44545.0833 | 9099.57
2021-12-15 03:00 | 44545.125 | 9116.162
2021-12-15 04:00 | 44545.1667 | 9596.323
2021-12-15 05:00 | 44545.2083 | 10667.27
2021-12-15 06:00 | 44545.25 | 11433.64
2021-12-15 07:00 | 44545.2917 | 11730.11
2021-12-15 08:00 | 44545.3333 | 11942.03
2021-12-15 09:00 | 44545.375 | 12032.44
2021-12-15 10:00 | 44545.4167 | 12124.8
2021-12-15 11:00 | 44545.4583 | 11987.44
2021-12-15 12:00 | 44545.5 | 11981.97
2021-12-15 13:00 | 44545.5417 | 11877.73
2021-12-15 14:00 | 44545.5833 | 11858.56
2021-12-15 15:00 | 44545.625 | 11893.74
2021-12-15 16:00 | 44545.6667 | 12451.18
2021-12-15 17:00 | 44545.7083 | 12571.67
2021-12-15 18:00 | 44545.75 | 12145.13
2021-12-15 19:00 | 44545.7917 | 11487.29
2021-12-15 20:00 | 44545.8333 | 10932.44
2021-12-15 21:00 | 44545.875 | 11151.19
2021-12-15 22:00 | 44545.9167 | 11086.9
2021-12-15 23:00 | 44545.9583 | 10386
2021-12-16 | 44546 | 9730.776
2021-12-16 01:00 | 44546.0417 | 9330.915
2021-12-16 02:00 | 44546.0833 | 9154.696
2021-12-16 03:00 | 44546.125 | 9168.192
2021-12-16 04:00 | 44546.1667 | 9637.65
2021-12-16 05:00 | 44546.2083 | 10699.23
2021-12-16 06:00 | 44546.25 | 11458.4
2021-12-16 07:00 | 44546.2917 | 11747.58
2021-12-16 08:00 | 44546.3333 | 11955.32
2021-12-16 09:00 | 44546.375 | 12042.07
2021-12-16 10:00 | 44546.4167 | 12137.07
2021-12-16 11:00 | 44546.4583 | 12002.92
2021-12-16 12:00 | 44546.5 | 12000.87
2021-12-16 13:00 | 44546.5417 | 11896.65
2021-12-16 14:00 | 44546.5833 | 11879.18
2021-12-16 15:00 | 44546.625 | 11913.49
2021-12-16 16:00 | 44546.6667 | 12471.01
2021-12-16 17:00 | 44546.7083 | 12591.64
2021-12-16 18:00 | 44546.75 | 12165.03
2021-12-16 19:00 | 44546.7917 | 11508.87
2021-12-16 20:00 | 44546.8333 | 10951.75
2021-12-16 21:00 | 44546.875 | 11176.29
2021-12-16 22:00 | 44546.9167 | 11124.22
2021-12-16 23:00 | 44546.9583 | 10432.27
2021-12-17 | 44547 | 9720.026
2021-12-17 01:00 | 44547.0417 | 9319.068
2021-12-17 02:00 | 44547.0833 | 9142.849
2021-12-17 03:00 | 44547.125 | 9154.571
2021-12-17 04:00 | 44547.1667 | 9629.886
2021-12-17 05:00 | 44547.2083 | 10694.71
2021-12-17 06:00 | 44547.25 | 11456.4
2021-12-17 07:00 | 44547.2917 | 11747.97
2021-12-17 08:00 | 44547.3333 | 11957.14
2021-12-17 09:00 | 44547.375 | 12045.05
2021-12-17 10:00 | 44547.4167 | 12139.43
2021-12-17 11:00 | 44547.4583 | 12004.29
2021-12-17 12:00 | 44547.5 | 12001.19
2021-12-17 13:00 | 44547.5417 | 11896.7
2021-12-17 14:00 | 44547.5833 | 11878.69
2021-12-17 15:00 | 44547.625 | 11913.26
2021-12-17 16:00 | 44547.6667 | 12471.01
2021-12-17 17:00 | 44547.7083 | 12591.68
2021-12-17 18:00 | 44547.75 | 12164.83
2021-12-17 19:00 | 44547.7917 | 11507.79
2021-12-17 20:00 | 44547.8333 | 10951.04
2021-12-17 21:00 | 44547.875 | 11173.94
2021-12-17 22:00 | 44547.9167 | 11118.13
2021-12-17 23:00 | 44547.9583 | 10423.09
2021-12-18 | 44548 | 9412.915
2021-12-18 01:00 | 44548.0417 | 9045.37
2021-12-18 02:00 | 44548.0833 | 8795.071
2021-12-18 03:00 | 44548.125 | 8682.766
2021-12-18 04:00 | 44548.1667 | 8664.572
2021-12-18 05:00 | 44548.2083 | 9040.65
2021-12-18 06:00 | 44548.25 | 9453.66
2021-12-18 07:00 | 44548.2917 | 9754.248
2021-12-18 08:00 | 44548.3333 | 10064.55
2021-12-18 09:00 | 44548.375 | 10215.75
2021-12-18 10:00 | 44548.4167 | 10448.93
2021-12-18 11:00 | 44548.4583 | 10345.84
2021-12-18 12:00 | 44548.5 | 10258.18
2021-12-18 13:00 | 44548.5417 | 10131
2021-12-18 14:00 | 44548.5833 | 10115.95
2021-12-18 15:00 | 44548.625 | 10158.25
2021-12-18 16:00 | 44548.6667 | 10705.27
2021-12-18 17:00 | 44548.7083 | 10982.16
2021-12-18 18:00 | 44548.75 | 10836.82
2021-12-18 19:00 | 44548.7917 | 10460.12
2021-12-18 20:00 | 44548.8333 | 10006.28
2021-12-18 21:00 | 44548.875 | 10256.44
2021-12-18 22:00 | 44548.9167 | 10339.07
2021-12-18 23:00 | 44548.9583 | 9850.222
2021-12-19 | 44549 | 9099.987
2021-12-19 01:00 | 44549.0417 | 8639.282
2021-12-19 02:00 | 44549.0833 | 8322.728
2021-12-19 03:00 | 44549.125 | 8121.844
2021-12-19 04:00 | 44549.1667 | 8002.282
2021-12-19 05:00 | 44549.2083 | 8215.811
2021-12-19 06:00 | 44549.25 | 8626.633
2021-12-19 07:00 | 44549.2917 | 9099.484
2021-12-19 08:00 | 44549.3333 | 9590.746
2021-12-19 09:00 | 44549.375 | 9863.862
2021-12-19 10:00 | 44549.4167 | 10191.76
2021-12-19 11:00 | 44549.4583 | 10042.71
2021-12-19 12:00 | 44549.5 | 9842.077
2021-12-19 13:00 | 44549.5417 | 9642.452
2021-12-19 14:00 | 44549.5833 | 9602.912
2021-12-19 15:00 | 44549.625 | 9677.455
2021-12-19 16:00 | 44549.6667 | 10341.6
2021-12-19 17:00 | 44549.7083 | 10767.74
2021-12-19 18:00 | 44549.75 | 10736.67
2021-12-19 19:00 | 44549.7917 | 10410.72
2021-12-19 20:00 | 44549.8333 | 9949.568
2021-12-19 21:00 | 44549.875 | 10181.55
2021-12-19 22:00 | 44549.9167 | 10178.03
2021-12-19 23:00 | 44549.9583 | 9567.649
2021-12-20 | 44550 | 8441.345
2021-12-20 01:00 | 44550.0417 | 8052.572
2021-12-20 02:00 | 44550.0833 | 7827.371
2021-12-20 03:00 | 44550.125 | 7792.648
2021-12-20 04:00 | 44550.1667 | 7940.286
2021-12-20 05:00 | 44550.2083 | 8444.963
2021-12-20 06:00 | 44550.25 | 8841.641
2021-12-20 07:00 | 44550.2917 | 9187.22
2021-12-20 08:00 | 44550.3333 | 9532.451
2021-12-20 09:00 | 44550.375 | 9764.61
2021-12-20 10:00 | 44550.4167 | 10014.3
2021-12-20 11:00 | 44550.4583 | 10038.73
2021-12-20 12:00 | 44550.5 | 9981.998
2021-12-20 13:00 | 44550.5417 | 9871.292
2021-12-20 14:00 | 44550.5833 | 9866.178
2021-12-20 15:00 | 44550.625 | 9975.036
2021-12-20 16:00 | 44550.6667 | 10650.65
2021-12-20 17:00 | 44550.7083 | 10816.45
2021-12-20 18:00 | 44550.75 | 10493.54
2021-12-20 19:00 | 44550.7917 | 9998.141
2021-12-20 20:00 | 44550.8333 | 9481.786
2021-12-20 21:00 | 44550.875 | 9691.26
2021-12-20 22:00 | 44550.9167 | 9703.955
2021-12-20 23:00 | 44550.9583 | 9129.174
2021-12-21 | 44551 | 8444.315
2021-12-21 01:00 | 44551.0417 | 8092.052
2021-12-21 02:00 | 44551.0833 | 7892.234
2021-12-21 03:00 | 44551.125 | 7891.022
2021-12-21 04:00 | 44551.1667 | 8088.018
2021-12-21 05:00 | 44551.2083 | 8585.988
2021-12-21 06:00 | 44551.25 | 8957.377
2021-12-21 07:00 | 44551.2917 | 9281.072
2021-12-21 08:00 | 44551.3333 | 9595.147
2021-12-21 09:00 | 44551.375 | 9813.457
2021-12-21 10:00 | 44551.4167 | 10023.3
2021-12-21 11:00 | 44551.4583 | 10051.96
2021-12-21 12:00 | 44551.5 | 10001.02
2021-12-21 13:00 | 44551.5417 | 9901.918
2021-12-21 14:00 | 44551.5833 | 9895.928
2021-12-21 15:00 | 44551.625 | 9999.731
2021-12-21 16:00 | 44551.6667 | 10604.15
2021-12-21 17:00 | 44551.7083 | 10727.55
2021-12-21 18:00 | 44551.75 | 10417.56
2021-12-21 19:00 | 44551.7917 | 9959.19
2021-12-21 20:00 | 44551.8333 | 9506.305
2021-12-21 21:00 | 44551.875 | 9668.357
2021-12-21 22:00 | 44551.9167 | 9635.869
2021-12-21 23:00 | 44551.9583 | 9097.068
2021-12-22 | 44552 | 8444.315
2021-12-22 01:00 | 44552.0417 | 8092.052
2021-12-22 02:00 | 44552.0833 | 7892.234
2021-12-22 03:00 | 44552.125 | 7891.022
2021-12-22 04:00 | 44552.1667 | 8088.018
2021-12-22 05:00 | 44552.2083 | 8585.988
2021-12-22 06:00 | 44552.25 | 8957.377
2021-12-22 07:00 | 44552.2917 | 9281.072
2021-12-22 08:00 | 44552.3333 | 9595.147
2021-12-22 09:00 | 44552.375 | 9813.457
2021-12-22 10:00 | 44552.4167 | 10023.3
2021-12-22 11:00 | 44552.4583 | 10051.96
2021-12-22 12:00 | 44552.5 | 10001.02
2021-12-22 13:00 | 44552.5417 | 9901.918
2021-12-22 14:00 | 44552.5833 | 9895.928
2021-12-22 15:00 | 44552.625 | 9999.731
2021-12-22 16:00 | 44552.6667 | 10604.15
2021-12-22 17:00 | 44552.7083 | 10727.55
2021-12-22 18:00 | 44552.75 | 10417.56
2021-12-22 19:00 | 44552.7917 | 9959.19
2021-12-22 20:00 | 44552.8333 | 9506.305
2021-12-22 21:00 | 44552.875 | 9668.357
2021-12-22 22:00 | 44552.9167 | 9635.869
2021-12-22 23:00 | 44552.9583 | 9097.068
2021-12-23 | 44553 | 8507.359
2021-12-23 01:00 | 44553.0417 | 8142.045
2021-12-23 02:00 | 44553.0833 | 7934.281
2021-12-23 03:00 | 44553.125 | 7918.573
2021-12-23 04:00 | 44553.1667 | 8101.798
2021-12-23 05:00 | 44553.2083 | 8606.111
2021-12-23 06:00 | 44553.25 | 8988.802
2021-12-23 07:00 | 44553.2917 | 9322.203
2021-12-23 08:00 | 44553.3333 | 9647.889
2021-12-23 09:00 | 44553.375 | 9872.696
2021-12-23 10:00 | 44553.4167 | 10095.33
2021-12-23 11:00 | 44553.4583 | 10121.71
2021-12-23 12:00 | 44553.5 | 10068.36
2021-12-23 13:00 | 44553.5417 | 9966.14
2021-12-23 14:00 | 44553.5833 | 9960.184
2021-12-23 15:00 | 44553.625 | 10066.97
2021-12-23 16:00 | 44553.6667 | 10694.06
2021-12-23 17:00 | 44553.7083 | 10837.12
2021-12-23 18:00 | 44553.75 | 10519.6
2021-12-23 19:00 | 44553.7917 | 10046.06
2021-12-23 20:00 | 44553.8333 | 9569.16
2021-12-23 21:00 | 44553.875 | 9748.306
2021-12-23 22:00 | 44553.9167 | 9730.869
2021-12-23 23:00 | 44553.9583 | 9176.682
2021-12-24 | 44554 | 8573.413
2021-12-24 01:00 | 44554.0417 | 8231.871
2021-12-24 02:00 | 44554.0833 | 8046.397
2021-12-24 03:00 | 44554.125 | 8035.35
2021-12-24 04:00 | 44554.1667 | 8240.084
2021-12-24 05:00 | 44554.2083 | 8734.188
2021-12-24 06:00 | 44554.25 | 9098.896
2021-12-24 07:00 | 44554.2917 | 9421.107
2021-12-24 08:00 | 44554.3333 | 9728.225
2021-12-24 09:00 | 44554.375 | 9945.003
2021-12-24 10:00 | 44554.4167 | 10147.67
2021-12-24 11:00 | 44554.4583 | 10176.76
2021-12-24 12:00 | 44554.5 | 10125.27
2021-12-24 13:00 | 44554.5417 | 10029.76
2021-12-24 14:00 | 44554.5833 | 10023.22
2021-12-24 15:00 | 44554.625 | 10126.83
2021-12-24 16:00 | 44554.6667 | 10709.62
2021-12-24 17:00 | 44554.7083 | 10835.72
2021-12-24 18:00 | 44554.75 | 10528.16
2021-12-24 19:00 | 44554.7917 | 10079.9
2021-12-24 20:00 | 44554.8333 | 9641.056
2021-12-24 21:00 | 44554.875 | 9793.095
2021-12-24 22:00 | 44554.9167 | 9751.213
2021-12-24 23:00 | 44554.9583 | 9220.334
2021-12-25 | 44555 | 8953.613
2021-12-25 01:00 | 44555.0417 | 8521.961
2021-12-25 02:00 | 44555.0833 | 8224.393
2021-12-25 03:00 | 44555.125 | 8053.819
2021-12-25 04:00 | 44555.1667 | 7981.644
2021-12-25 05:00 | 44555.2083 | 8287.756
2021-12-25 06:00 | 44555.25 | 8718.775
2021-12-25 07:00 | 44555.2917 | 9112.824
2021-12-25 08:00 | 44555.3333 | 9525.32
2021-12-25 09:00 | 44555.375 | 9740.561
2021-12-25 10:00 | 44555.4167 | 10037.58
2021-12-25 11:00 | 44555.4583 | 9909.611
2021-12-25 12:00 | 44555.5 | 9765.972
2021-12-25 13:00 | 44555.5417 | 9597.526
2021-12-25 14:00 | 44555.5833 | 9571.149
2021-12-25 15:00 | 44555.625 | 9630.743
2021-12-25 16:00 | 44555.6667 | 10270.31
2021-12-25 17:00 | 44555.7083 | 10640.43
2021-12-25 18:00 | 44555.75 | 10535.88
2021-12-25 19:00 | 44555.7917 | 10161.07
2021-12-25 20:00 | 44555.8333 | 9670.782
2021-12-25 21:00 | 44555.875 | 9934.825
2021-12-25 22:00 | 44555.9167 | 9995.22
2021-12-25 23:00 | 44555.9583 | 9426.047
2021-12-26 | 44556 | 9232.388
2021-12-26 01:00 | 44556.0417 | 8770.167
2021-12-26 02:00 | 44556.0833 | 8452.914
2021-12-26 03:00 | 44556.125 | 8253.738
2021-12-26 04:00 | 44556.1667 | 8129.863
2021-12-26 05:00 | 44556.2083 | 8339.408
2021-12-26 06:00 | 44556.25 | 8748.572
2021-12-26 07:00 | 44556.2917 | 9226.588
2021-12-26 08:00 | 44556.3333 | 9722.575
2021-12-26 09:00 | 44556.375 | 9999.668
2021-12-26 10:00 | 44556.4167 | 10329.02
2021-12-26 11:00 | 44556.4583 | 10178.69
2021-12-26 12:00 | 44556.5 | 9974.527
2021-12-26 13:00 | 44556.5417 | 9770.306
2021-12-26 14:00 | 44556.5833 | 9730.234
2021-12-26 15:00 | 44556.625 | 9806.426
2021-12-26 16:00 | 44556.6667 | 10471.68
2021-12-26 17:00 | 44556.7083 | 10900.75
2021-12-26 18:00 | 44556.75 | 10873.44
2021-12-26 19:00 | 44556.7917 | 10551.64
2021-12-26 20:00 | 44556.8333 | 10093.28
2021-12-26 21:00 | 44556.875 | 10322.17
2021-12-26 22:00 | 44556.9167 | 10313.07
2021-12-26 23:00 | 44556.9583 | 9699.856
2021-12-27 | 44557 | 8573.413
2021-12-27 01:00 | 44557.0417 | 8231.871
2021-12-27 02:00 | 44557.0833 | 8046.397
2021-12-27 03:00 | 44557.125 | 8035.35
2021-12-27 04:00 | 44557.1667 | 8240.084
2021-12-27 05:00 | 44557.2083 | 8734.188
2021-12-27 06:00 | 44557.25 | 9098.896
2021-12-27 07:00 | 44557.2917 | 9421.107
2021-12-27 08:00 | 44557.3333 | 9728.225
2021-12-27 09:00 | 44557.375 | 9945.003
2021-12-27 10:00 | 44557.4167 | 10147.67
2021-12-27 11:00 | 44557.4583 | 10176.76
2021-12-27 12:00 | 44557.5 | 10125.27
2021-12-27 13:00 | 44557.5417 | 10029.76
2021-12-27 14:00 | 44557.5833 | 10023.22
2021-12-27 15:00 | 44557.625 | 10126.83
2021-12-27 16:00 | 44557.6667 | 10709.62
2021-12-27 17:00 | 44557.7083 | 10835.72
2021-12-27 18:00 | 44557.75 | 10528.16
2021-12-27 19:00 | 44557.7917 | 10079.9
2021-12-27 20:00 | 44557.8333 | 9641.056
2021-12-27 21:00 | 44557.875 | 9793.095
2021-12-27 22:00 | 44557.9167 | 9751.213
2021-12-27 23:00 | 44557.9583 | 9220.334
2021-12-28 | 44558 | 8573.413
2021-12-28 01:00 | 44558.0417 | 8231.871
2021-12-28 02:00 | 44558.0833 | 8046.397
2021-12-28 03:00 | 44558.125 | 8035.35
2021-12-28 04:00 | 44558.1667 | 8240.084
2021-12-28 05:00 | 44558.2083 | 8734.188
2021-12-28 06:00 | 44558.25 | 9098.896
2021-12-28 07:00 | 44558.2917 | 9421.107
2021-12-28 08:00 | 44558.3333 | 9728.225
2021-12-28 09:00 | 44558.375 | 9945.003
2021-12-28 10:00 | 44558.4167 | 10147.67
2021-12-28 11:00 | 44558.4583 | 10176.76
2021-12-28 12:00 | 44558.5 | 10125.27
2021-12-28 13:00 | 44558.5417 | 10029.76
2021-12-28 14:00 | 44558.5833 | 10023.22
2021-12-28 15:00 | 44558.625 | 10126.83
2021-12-28 16:00 | 44558.6667 | 10709.62
2021-12-28 17:00 | 44558.7083 | 10835.72
2021-12-28 18:00 | 44558.75 | 10528.16
2021-12-28 19:00 | 44558.7917 | 10079.9
2021-12-28 20:00 | 44558.8333 | 9641.056
2021-12-28 21:00 | 44558.875 | 9793.095
2021-12-28 22:00 | 44558.9167 | 9751.213
2021-12-28 23:00 | 44558.9583 | 9220.334
2021-12-29 | 44559 | 8573.413
2021-12-29 01:00 | 44559.0417 | 8231.871
2021-12-29 02:00 | 44559.0833 | 8046.397
2021-12-29 03:00 | 44559.125 | 8035.35
2021-12-29 04:00 | 44559.1667 | 8240.084
2021-12-29 05:00 | 44559.2083 | 8734.188
2021-12-29 06:00 | 44559.25 | 9098.896
2021-12-29 07:00 | 44559.2917 | 9421.107
2021-12-29 08:00 | 44559.3333 | 9728.225
2021-12-29 09:00 | 44559.375 | 9945.003
2021-12-29 10:00 | 44559.4167 | 10147.67
2021-12-29 11:00 | 44559.4583 | 10176.76
2021-12-29 12:00 | 44559.5 | 10125.27
2021-12-29 13:00 | 44559.5417 | 10029.76
2021-12-29 14:00 | 44559.5833 | 10023.22
2021-12-29 15:00 | 44559.625 | 10126.83
2021-12-29 16:00 | 44559.6667 | 10709.62
2021-12-29 17:00 | 44559.7083 | 10835.72
2021-12-29 18:00 | 44559.75 | 10528.16
2021-12-29 19:00 | 44559.7917 | 10079.9
2021-12-29 20:00 | 44559.8333 | 9641.056
2021-12-29 21:00 | 44559.875 | 9793.095
2021-12-29 22:00 | 44559.9167 | 9751.213
2021-12-29 23:00 | 44559.9583 | 9220.334
2021-12-30 | 44560 | 8573.413
2021-12-30 01:00 | 44560.0417 | 8231.871
2021-12-30 02:00 | 44560.0833 | 8046.397
2021-12-30 03:00 | 44560.125 | 8035.35
2021-12-30 04:00 | 44560.1667 | 8240.084
2021-12-30 05:00 | 44560.2083 | 8734.188
2021-12-30 06:00 | 44560.25 | 9098.896
2021-12-30 07:00 | 44560.2917 | 9421.107
2021-12-30 08:00 | 44560.3333 | 9728.225
2021-12-30 09:00 | 44560.375 | 9945.003
2021-12-30 10:00 | 44560.4167 | 10147.67
2021-12-30 11:00 | 44560.4583 | 10176.76
2021-12-30 12:00 | 44560.5 | 10125.27
2021-12-30 13:00 | 44560.5417 | 10029.76
2021-12-30 14:00 | 44560.5833 | 10023.22
2021-12-30 15:00 | 44560.625 | 10126.83
2021-12-30 16:00 | 44560.6667 | 10709.62
2021-12-30 17:00 | 44560.7083 | 10835.72
2021-12-30 18:00 | 44560.75 | 10528.16
2021-12-30 19:00 | 44560.7917 | 10079.9
2021-12-30 20:00 | 44560.8333 | 9641.056
2021-12-30 21:00 | 44560.875 | 9793.095
2021-12-30 22:00 | 44560.9167 | 9751.213
2021-12-30 23:00 | 44560.9583 | 9220.334
2021-12-31 | 44561 | 8560.264
2021-12-31 01:00 | 44561.0417 | 8233.653
2021-12-31 02:00 | 44561.0833 | 8064.866
2021-12-31 03:00 | 44561.125 | 8079.726
2021-12-31 04:00 | 44561.1667 | 8307.335
2021-12-31 05:00 | 44561.2083 | 8805.005
2021-12-31 06:00 | 44561.25 | 9157.657
2021-12-31 07:00 | 44561.2917 | 9468.582
2021-12-31 08:00 | 44561.3333 | 9756.345
2021-12-31 09:00 | 44561.375 | 9966.832
2021-12-31 10:00 | 44561.4167 | 10145.33
2021-12-31 11:00 | 44561.4583 | 10177.13
2021-12-31 12:00 | 44561.5 | 10130.85
2021-12-31 13:00 | 44561.5417 | 10042.04
2021-12-31 14:00 | 44561.5833 | 10035.56
2021-12-31 15:00 | 44561.625 | 10138.54
2021-12-31 16:00 | 44561.6667 | 10687.18
2021-12-31 17:00 | 44561.7083 | 10782.31
2021-12-31 18:00 | 44561.75 | 10480.23
2021-12-31 19:00 | 44561.7917 | 10047.25
2021-12-31 20:00 | 44561.8333 | 9638.25
2021-12-31 21:00 | 44561.875 | 9767.879
2021-12-31 22:00 | 44561.9167 | 9705.8
2021-12-31 23:00 | 44561.9583 | 9192.778
2022-01-01 | 44562 | 9142.718
2022-01-01 01:00 | 44562.0417 | 8709.008
2022-01-01 02:00 | 44562.0833 | 8411.48
2022-01-01 03:00 | 44562.125 | 8244.153
2022-01-01 04:00 | 44562.1667 | 8173.185
2022-01-01 05:00 | 44562.2083 | 8475.069
2022-01-01 06:00 | 44562.25 | 8906.442
2022-01-01 07:00 | 44562.2917 | 9310.334
2022-01-01 08:00 | 44562.3333 | 9730.419
2022-01-01 09:00 | 44562.375 | 9952.131
2022-01-01 10:00 | 44562.4167 | 10248.8
2022-01-01 11:00 | 44562.4583 | 10117.76
2022-01-01 12:00 | 44562.5 | 9967.643
2022-01-01 13:00 | 44562.5417 | 9795.085
2022-01-01 14:00 | 44562.5833 | 9766.847
2022-01-01 15:00 | 44562.625 | 9828.518
2022-01-01 16:00 | 44562.6667 | 10466.55
2022-01-01 17:00 | 44562.7083 | 10841.37
2022-01-01 18:00 | 44562.75 | 10739.92
2022-01-01 19:00 | 44562.7917 | 10373.14
2022-01-01 20:00 | 44562.8333 | 9890.038
2022-01-01 21:00 | 44562.875 | 10145.68
2022-01-01 22:00 | 44562.9167 | 10191.59
2022-01-01 23:00 | 44562.9583 | 9615.961
2022-01-02 | 44563 | 8511.453
2022-01-02 01:00 | 44563.0417 | 8191.038
2022-01-02 02:00 | 44563.0833 | 8021.824
2022-01-02 03:00 | 44563.125 | 8044.93
2022-01-02 04:00 | 44563.1667 | 8279.184
2022-01-02 05:00 | 44563.2083 | 8783.309
2022-01-02 06:00 | 44563.25 | 9139.347
2022-01-02 07:00 | 44563.2917 | 9449.402
2022-01-02 08:00 | 44563.3333 | 9736.605
2022-01-02 09:00 | 44563.375 | 9947.367
2022-01-02 10:00 | 44563.4167 | 10120.49
2022-01-02 11:00 | 44563.4583 | 10151.04
2022-01-02 12:00 | 44563.5 | 10103.52
2022-01-02 13:00 | 44563.5417 | 10014.46
2022-01-02 14:00 | 44563.5833 | 10007.14
2022-01-02 15:00 | 44563.625 | 10109.62
2022-01-02 16:00 | 44563.6667 | 10649.43
2022-01-02 17:00 | 44563.7083 | 10742.4
2022-01-02 18:00 | 44563.75 | 10441.06
2022-01-02 19:00 | 44563.7917 | 10011.46
2022-01-02 20:00 | 44563.8333 | 9611.076
2022-01-02 21:00 | 44563.875 | 9731.928
2022-01-02 22:00 | 44563.9167 | 9657.106
2022-01-02 23:00 | 44563.9583 | 9143.431
2022-01-03 | 44564 | 8656.413
2022-01-03 01:00 | 44564.0417 | 8280.463
2022-01-03 02:00 | 44564.0833 | 8058.413
2022-01-03 03:00 | 44564.125 | 8028.137
2022-01-03 04:00 | 44564.1667 | 8179.013
2022-01-03 05:00 | 44564.2083 | 8654.574
2022-01-03 06:00 | 44564.25 | 9030.309
2022-01-03 07:00 | 44564.2917 | 9368.536
2022-01-03 08:00 | 44564.3333 | 9705.93
2022-01-03 09:00 | 44564.375 | 9935.36
2022-01-03 10:00 | 44564.4167 | 10176.93
2022-01-03 11:00 | 44564.4583 | 10204.13
2022-01-03 12:00 | 44564.5 | 10146.77
2022-01-03 13:00 | 44564.5417 | 10039.71
2022-01-03 14:00 | 44564.5833 | 10034.81
2022-01-03 15:00 | 44564.625 | 10141.44
2022-01-03 16:00 | 44564.6667 | 10791.22
2022-01-03 17:00 | 44564.7083 | 10956.02
2022-01-03 18:00 | 44564.75 | 10642.88
2022-01-03 19:00 | 44564.7917 | 10169.2
2022-01-03 20:00 | 44564.8333 | 9676.363
2022-01-03 21:00 | 44564.875 | 9872.45
2022-01-03 22:00 | 44564.9167 | 9877.247
2022-01-03 23:00 | 44564.9583 | 9322.392
2022-01-04 | 44565 | 8610.496
2022-01-04 01:00 | 44565.0417 | 8249.318
2022-01-04 02:00 | 44565.0833 | 8054.31
2022-01-04 03:00 | 44565.125 | 8039.856
2022-01-04 04:00 | 44565.1667 | 8212.523
2022-01-04 05:00 | 44565.2083 | 8699.099
2022-01-04 06:00 | 44565.25 | 9067.44
2022-01-04 07:00 | 44565.2917 | 9398.582
2022-01-04 08:00 | 44565.3333 | 9719.806
2022-01-04 09:00 | 44565.375 | 9944.076
2022-01-04 10:00 | 44565.4167 | 10162.73
2022-01-04 11:00 | 44565.4583 | 10190.75
2022-01-04 12:00 | 44565.5 | 10136.16
2022-01-04 13:00 | 44565.5417 | 10034.93
2022-01-04 14:00 | 44565.5833 | 10029.1
2022-01-04 15:00 | 44565.625 | 10135.85
2022-01-04 16:00 | 44565.6667 | 10752.73
2022-01-04 17:00 | 44565.7083 | 10884.2
2022-01-04 18:00 | 44565.75 | 10580.8
2022-01-04 19:00 | 44565.7917 | 10121.92
2022-01-04 20:00 | 44565.8333 | 9659.855
2022-01-04 21:00 | 44565.875 | 9830.668
2022-01-04 22:00 | 44565.9167 | 9808.278
2022-01-04 23:00 | 44565.9583 | 9266.373
2022-01-05 | 44566 | 8585.538
2022-01-05 01:00 | 44566.0417 | 8218.109
2022-01-05 02:00 | 44566.0833 | 8013.399
2022-01-05 03:00 | 44566.125 | 7988.846
2022-01-05 04:00 | 44566.1667 | 8157.489
2022-01-05 05:00 | 44566.2083 | 8655.426
2022-01-05 06:00 | 44566.25 | 9035.464
2022-01-05 07:00 | 44566.2917 | 9368.329
2022-01-05 08:00 | 44566.3333 | 9695.037
2022-01-05 09:00 | 44566.375 | 9920.154
2022-01-05 10:00 | 44566.4167 | 10148.42
2022-01-05 11:00 | 44566.4583 | 10175.95
2022-01-05 12:00 | 44566.5 | 10122.64
2022-01-05 13:00 | 44566.5417 | 10017.85
2022-01-05 14:00 | 44566.5833 | 10012.85
2022-01-05 15:00 | 44566.625 | 10120.18
2022-01-05 16:00 | 44566.6667 | 10754.92
2022-01-05 17:00 | 44566.7083 | 10898.47
2022-01-05 18:00 | 44566.75 | 10584.79
2022-01-05 19:00 | 44566.7917 | 10111.28
2022-01-05 20:00 | 44566.8333 | 9629.479
2022-01-05 21:00 | 44566.875 | 9814.489
2022-01-05 22:00 | 44566.9167 | 9805.831
2022-01-05 23:00 | 44566.9583 | 9253.506
2022-01-06 | 44567 | 9461.532
2022-01-06 01:00 | 44567.0417 | 9088.374
2022-01-06 02:00 | 44567.0833 | 8840.584
2022-01-06 03:00 | 44567.125 | 8746.568
2022-01-06 04:00 | 44567.1667 | 8741.062
2022-01-06 05:00 | 44567.2083 | 9139.949
2022-01-06 06:00 | 44567.25 | 9567.381
2022-01-06 07:00 | 44567.2917 | 9892.856
2022-01-06 08:00 | 44567.3333 | 10218.23
2022-01-06 09:00 | 44567.375 | 10384.14
2022-01-06 10:00 | 44567.4167 | 10609.54
2022-01-06 11:00 | 44567.4583 | 10497
2022-01-06 12:00 | 44567.5 | 10395.57
2022-01-06 13:00 | 44567.5417 | 10259.52
2022-01-06 14:00 | 44567.5833 | 10239.47
2022-01-06 15:00 | 44567.625 | 10286.75
2022-01-06 16:00 | 44567.6667 | 10828.55
2022-01-06 17:00 | 44567.7083 | 11104.97
2022-01-06 18:00 | 44567.75 | 10969.03
2022-01-06 19:00 | 44567.7917 | 10597.23
2022-01-06 20:00 | 44567.8333 | 10160.11
2022-01-06 21:00 | 44567.875 | 10385.82
2022-01-06 22:00 | 44567.9167 | 10423.78
2022-01-06 23:00 | 44567.9583 | 9911.004
2022-01-07 | 44568 | 9231.864
2022-01-07 01:00 | 44568.0417 | 8773.659
2022-01-07 02:00 | 44568.0833 | 8461.118
2022-01-07 03:00 | 44568.125 | 8266.357
2022-01-07 04:00 | 44568.1667 | 8141.817
2022-01-07 05:00 | 44568.2083 | 8332.738
2022-01-07 06:00 | 44568.25 | 8731.565
2022-01-07 07:00 | 44568.2917 | 9219.967
2022-01-07 08:00 | 44568.3333 | 9722.972
2022-01-07 09:00 | 44568.375 | 10008.17
2022-01-07 10:00 | 44568.4167 | 10332.33
2022-01-07 11:00 | 44568.4583 | 10178.47
2022-01-07 12:00 | 44568.5 | 9964.202
2022-01-07 13:00 | 44568.5417 | 9759.666
2022-01-07 14:00 | 44568.5833 | 9716.699
2022-01-07 15:00 | 44568.625 | 9794.988
2022-01-07 16:00 | 44568.6667 | 10445.26
2022-01-07 17:00 | 44568.7083 | 10873.09
2022-01-07 18:00 | 44568.75 | 10864.49
2022-01-07 19:00 | 44568.7917 | 10562.12
2022-01-07 20:00 | 44568.8333 | 10126.2
2022-01-07 21:00 | 44568.875 | 10336.21
2022-01-07 22:00 | 44568.9167 | 10302.43
2022-01-07 23:00 | 44568.9583 | 9690.379
2022-01-08 | 44569 | 9892.345
2022-01-08 01:00 | 44569.0417 | 9498.565
2022-01-08 02:00 | 44569.0833 | 9325.915
2022-01-08 03:00 | 44569.125 | 9337.009
2022-01-08 04:00 | 44569.1667 | 9794.812
2022-01-08 05:00 | 44569.2083 | 10815.86
2022-01-08 06:00 | 44569.25 | 11553.26
2022-01-08 07:00 | 44569.2917 | 11852.33
2022-01-08 08:00 | 44569.3333 | 12069.18
2022-01-08 09:00 | 44569.375 | 12165.7
2022-01-08 10:00 | 44569.4167 | 12258.86
2022-01-08 11:00 | 44569.4583 | 12122.72
2022-01-08 12:00 | 44569.5 | 12108.54
2022-01-08 13:00 | 44569.5417 | 12001.45
2022-01-08 14:00 | 44569.5833 | 11981.54
2022-01-08 15:00 | 44569.625 | 12018.48
2022-01-08 16:00 | 44569.6667 | 12559.09
2022-01-08 17:00 | 44569.7083 | 12682.16
2022-01-08 18:00 | 44569.75 | 12283.36
2022-01-08 19:00 | 44569.7917 | 11656.28
2022-01-08 20:00 | 44569.8333 | 11126.42
2022-01-08 21:00 | 44569.875 | 11331.84
2022-01-08 22:00 | 44569.9167 | 11258.57
2022-01-08 23:00 | 44569.9583 | 10575.43
2022-01-09 | 44570 | 9857.737
2022-01-09 01:00 | 44570.0417 | 9458.465
2022-01-09 02:00 | 44570.0833 | 9281.188
2022-01-09 03:00 | 44570.125 | 9292.101
2022-01-09 04:00 | 44570.1667 | 9751.578
2022-01-09 05:00 | 44570.2083 | 10793.66
2022-01-09 06:00 | 44570.25 | 11543.58
2022-01-09 07:00 | 44570.2917 | 11837.97
2022-01-09 08:00 | 44570.3333 | 12051.69
2022-01-09 09:00 | 44570.375 | 12143.14
2022-01-09 10:00 | 44570.4167 | 12239.9
2022-01-09 11:00 | 44570.4583 | 12104.68
2022-01-09 12:00 | 44570.5 | 12096.93
2022-01-09 13:00 | 44570.5417 | 11991.99
2022-01-09 14:00 | 44570.5833 | 11973.81
2022-01-09 15:00 | 44570.625 | 12009.52
2022-01-09 16:00 | 44570.6667 | 12563.25
2022-01-09 17:00 | 44570.7083 | 12687.92
2022-01-09 18:00 | 44570.75 | 12273.2
2022-01-09 19:00 | 44570.7917 | 11628.34
2022-01-09 20:00 | 44570.8333 | 11079.54
2022-01-09 21:00 | 44570.875 | 11298.9
2022-01-09 22:00 | 44570.9167 | 11241.16
2022-01-09 23:00 | 44570.9583 | 10551.85
2022-01-10 | 44571 | 9873.999
2022-01-10 01:00 | 44571.0417 | 9478.829
2022-01-10 02:00 | 44571.0833 | 9305.672
2022-01-10 03:00 | 44571.125 | 9317.372
2022-01-10 04:00 | 44571.1667 | 9775.718
2022-01-10 05:00 | 44571.2083 | 10802.98
2022-01-10 06:00 | 44571.25 | 11544.04
2022-01-10 07:00 | 44571.2917 | 11842.11
2022-01-10 08:00 | 44571.3333 | 12058.11
2022-01-10 09:00 | 44571.375 | 12153.43
2022-01-10 10:00 | 44571.4167 | 12246.96
2022-01-10 11:00 | 44571.4583 | 12110.85
2022-01-10 12:00 | 44571.5 | 12098.25
2022-01-10 13:00 | 44571.5417 | 11991.94
2022-01-10 14:00 | 44571.5833 | 11972.37
2022-01-10 15:00 | 44571.625 | 12009.07
2022-01-10 16:00 | 44571.6667 | 12552.68
2022-01-10 17:00 | 44571.7083 | 12675.84
2022-01-10 18:00 | 44571.75 | 12272.78
2022-01-10 19:00 | 44571.7917 | 11640.99
2022-01-10 20:00 | 44571.8333 | 11106.52
2022-01-10 21:00 | 44571.875 | 11315.09
2022-01-10 22:00 | 44571.9167 | 11245.05
2022-01-10 23:00 | 44571.9583 | 10559.95
2022-01-11 | 44572 | 9886.383
2022-01-11 01:00 | 44572.0417 | 9492.799
2022-01-11 02:00 | 44572.0833 | 9320.333
2022-01-11 03:00 | 44572.125 | 9333.612
2022-01-11 04:00 | 44572.1667 | 9791.034
2022-01-11 05:00 | 44572.2083 | 10816.74
2022-01-11 06:00 | 44572.25 | 11555.94
2022-01-11 07:00 | 44572.2917 | 11852.26
2022-01-11 08:00 | 44572.3333 | 12066.59
2022-01-11 09:00 | 44572.375 | 12160.79
2022-01-11 10:00 | 44572.4167 | 12253.48
2022-01-11 11:00 | 44572.4583 | 12118
2022-01-11 12:00 | 44572.5 | 12106.13
2022-01-11 13:00 | 44572.5417 | 12000.57
2022-01-11 14:00 | 44572.5833 | 11981.27
2022-01-11 15:00 | 44572.625 | 12017.67
2022-01-11 16:00 | 44572.6667 | 12558.91
2022-01-11 17:00 | 44572.7083 | 12680.58
2022-01-11 18:00 | 44572.75 | 12278.03
2022-01-11 19:00 | 44572.7917 | 11647.68
2022-01-11 20:00 | 44572.8333 | 11114.87
2022-01-11 21:00 | 44572.875 | 11322.89
2022-01-11 22:00 | 44572.9167 | 11253.36
2022-01-11 23:00 | 44572.9583 | 10570.8
2022-01-12 | 44573 | 9905.641
2022-01-12 01:00 | 44573.0417 | 9515.035
2022-01-12 02:00 | 44573.0833 | 9344.218
2022-01-12 03:00 | 44573.125 | 9355.518
2022-01-12 04:00 | 44573.1667 | 9808.059
2022-01-12 05:00 | 44573.2083 | 10816.4
2022-01-12 06:00 | 44573.25 | 11545.92
2022-01-12 07:00 | 44573.2917 | 11845.25
2022-01-12 08:00 | 44573.3333 | 12062.57
2022-01-12 09:00 | 44573.375 | 12160.5
2022-01-12 10:00 | 44573.4167 | 12252.26
2022-01-12 11:00 | 44573.4583 | 12116.28
2022-01-12 12:00 | 44573.5 | 12099.85
2022-01-12 13:00 | 44573.5417 | 11993.29
2022-01-12 14:00 | 44573.5833 | 11973.03
2022-01-12 15:00 | 44573.625 | 12010.23
2022-01-12 16:00 | 44573.6667 | 12544.6
2022-01-12 17:00 | 44573.7083 | 12667.07
2022-01-12 18:00 | 44573.75 | 12275.73
2022-01-12 19:00 | 44573.7917 | 11657.4
2022-01-12 20:00 | 44573.8333 | 11135.59
2022-01-12 21:00 | 44573.875 | 11336.3
2022-01-12 22:00 | 44573.9167 | 11259.34
2022-01-12 23:00 | 44573.9583 | 10581.46
2022-01-13 | 44574 | 9523.83
2022-01-13 01:00 | 44574.0417 | 9157.496
2022-01-13 02:00 | 44574.0833 | 8912.594
2022-01-13 03:00 | 44574.125 | 8809.373
2022-01-13 04:00 | 44574.1667 | 8798.579
2022-01-13 05:00 | 44574.2083 | 9157.564
2022-01-13 06:00 | 44574.25 | 9564.708
2022-01-13 07:00 | 44574.2917 | 9888.373
2022-01-13 08:00 | 44574.3333 | 10214.34
2022-01-13 09:00 | 44574.375 | 10381.86
2022-01-13 10:00 | 44574.4167 | 10607.27
2022-01-13 11:00 | 44574.4583 | 10496.18
2022-01-13 12:00 | 44574.5 | 10390.81
2022-01-13 13:00 | 44574.5417 | 10257.24
2022-01-13 14:00 | 44574.5833 | 10237.16
2022-01-13 15:00 | 44574.625 | 10284.43
2022-01-13 16:00 | 44574.6667 | 10814.4
2022-01-13 17:00 | 44574.7083 | 11091.72
2022-01-13 18:00 | 44574.75 | 10972.3
2022-01-13 19:00 | 44574.7917 | 10619.81
2022-01-13 20:00 | 44574.8333 | 10197.41
2022-01-13 21:00 | 44574.875 | 10416.95
2022-01-13 22:00 | 44574.9167 | 10453.94
2022-01-13 23:00 | 44574.9583 | 9955.827
2022-01-14 | 44575 | 9259.963
2022-01-14 01:00 | 44575.0417 | 8799.06
2022-01-14 02:00 | 44575.0833 | 8485.637
2022-01-14 03:00 | 44575.125 | 8292.13
2022-01-14 04:00 | 44575.1667 | 8168.555
2022-01-14 05:00 | 44575.2083 | 8359.575
2022-01-14 06:00 | 44575.25 | 8757.81
2022-01-14 07:00 | 44575.2917 | 9253.877
2022-01-14 08:00 | 44575.3333 | 9763.165
2022-01-14 09:00 | 44575.375 | 10053.27
2022-01-14 10:00 | 44575.4167 | 10377.37
2022-01-14 11:00 | 44575.4583 | 10220.79
2022-01-14 12:00 | 44575.5 | 10001.77
2022-01-14 13:00 | 44575.5417 | 9796.143
2022-01-14 14:00 | 44575.5833 | 9751.823
2022-01-14 15:00 | 44575.625 | 9831.336
2022-01-14 16:00 | 44575.6667 | 10482.32
2022-01-14 17:00 | 44575.7083 | 10913.31
2022-01-14 18:00 | 44575.75 | 10903.48
2022-01-14 19:00 | 44575.7917 | 10609.28
2022-01-14 20:00 | 44575.8333 | 10176.47
2022-01-14 21:00 | 44575.875 | 10381.88
2022-01-14 22:00 | 44575.9167 | 10338.85
2022-01-14 23:00 | 44575.9583 | 9720.697
2022-01-15 | 44576 | 9887.535
2022-01-15 01:00 | 44576.0417 | 9494.131
2022-01-15 02:00 | 44576.0833 | 9320.865
2022-01-15 03:00 | 44576.125 | 9332.545
2022-01-15 04:00 | 44576.1667 | 9781.239
2022-01-15 05:00 | 44576.2083 | 10793.93
2022-01-15 06:00 | 44576.25 | 11526.98
2022-01-15 07:00 | 44576.2917 | 11826.16
2022-01-15 08:00 | 44576.3333 | 12044.29
2022-01-15 09:00 | 44576.375 | 12141.5
2022-01-15 10:00 | 44576.4167 | 12235.87
2022-01-15 11:00 | 44576.4583 | 12099.87
2022-01-15 12:00 | 44576.5 | 12084.56
2022-01-15 13:00 | 44576.5417 | 11978.52
2022-01-15 14:00 | 44576.5833 | 11958.59
2022-01-15 15:00 | 44576.625 | 11995.74
2022-01-15 16:00 | 44576.6667 | 12535.69
2022-01-15 17:00 | 44576.7083 | 12660.61
2022-01-15 18:00 | 44576.75 | 12265.31
2022-01-15 19:00 | 44576.7917 | 11641.72
2022-01-15 20:00 | 44576.8333 | 11113.14
2022-01-15 21:00 | 44576.875 | 11318.92
2022-01-15 22:00 | 44576.9167 | 11247.36
2022-01-15 23:00 | 44576.9583 | 10566.75
2022-01-16 | 44577 | 9905.523
2022-01-16 01:00 | 44577.0417 | 9520.767
2022-01-16 02:00 | 44577.0833 | 9355.156
2022-01-16 03:00 | 44577.125 | 9370.445
2022-01-16 04:00 | 44577.1667 | 9823.41
2022-01-16 05:00 | 44577.2083 | 10817.34
2022-01-16 06:00 | 44577.25 | 11537.13
2022-01-16 07:00 | 44577.2917 | 11839.02
2022-01-16 08:00 | 44577.3333 | 12056.86
2022-01-16 09:00 | 44577.375 | 12157.62
2022-01-16 10:00 | 44577.4167 | 12244.22
2022-01-16 11:00 | 44577.4583 | 12107.36
2022-01-16 12:00 | 44577.5 | 12086.36
2022-01-16 13:00 | 44577.5417 | 11979.72
2022-01-16 14:00 | 44577.5833 | 11958.17
2022-01-16 15:00 | 44577.625 | 11996.18
2022-01-16 16:00 | 44577.6667 | 12516.59
2022-01-16 17:00 | 44577.7083 | 12635.26
2022-01-16 18:00 | 44577.75 | 12256.11
2022-01-16 19:00 | 44577.7917 | 11652.4
2022-01-16 20:00 | 44577.8333 | 11147.8
2022-01-16 21:00 | 44577.875 | 11335.54
2022-01-16 22:00 | 44577.9167 | 11244.17
2022-01-16 23:00 | 44577.9583 | 10572.13
2022-01-17 | 44578 | 9861.83
2022-01-17 01:00 | 44578.0417 | 9478.615
2022-01-17 02:00 | 44578.0833 | 9315.334
2022-01-17 03:00 | 44578.125 | 9330.211
2022-01-17 04:00 | 44578.1667 | 9785.844
2022-01-17 05:00 | 44578.2083 | 10776.46
2022-01-17 06:00 | 44578.25 | 11494.06
2022-01-17 07:00 | 44578.2917 | 11797.43
2022-01-17 08:00 | 44578.3333 | 12015.78
2022-01-17 09:00 | 44578.375 | 12117.7
2022-01-17 10:00 | 44578.4167 | 12202.53
2022-01-17 11:00 | 44578.4583 | 12065.14
2022-01-17 12:00 | 44578.5 | 12042.47
2022-01-17 13:00 | 44578.5417 | 11935.39
2022-01-17 14:00 | 44578.5833 | 11913.25
2022-01-17 15:00 | 44578.625 | 11951.58
2022-01-17 16:00 | 44578.6667 | 12467.87
2022-01-17 17:00 | 44578.7083 | 12585.25
2022-01-17 18:00 | 44578.75 | 12209.78
2022-01-17 19:00 | 44578.7917 | 11610.3
2022-01-17 20:00 | 44578.8333 | 11111.21
2022-01-17 21:00 | 44578.875 | 11294.38
2022-01-17 22:00 | 44578.9167 | 11197.31
2022-01-17 23:00 | 44578.9583 | 10526.12
2022-01-18 | 44579 | 9861.661
2022-01-18 01:00 | 44579.0417 | 9474.121
2022-01-18 02:00 | 44579.0833 | 9307.784
2022-01-18 03:00 | 44579.125 | 9324.85
2022-01-18 04:00 | 44579.1667 | 9779.234
2022-01-18 05:00 | 44579.2083 | 10780.67
2022-01-18 06:00 | 44579.25 | 11505.97
2022-01-18 07:00 | 44579.2917 | 11810.14
2022-01-18 08:00 | 44579.3333 | 12029.64
2022-01-18 09:00 | 44579.375 | 12131.19
2022-01-18 10:00 | 44579.4167 | 12217.74
2022-01-18 11:00 | 44579.4583 | 12079.65
2022-01-18 12:00 | 44579.5 | 12058.44
2022-01-18 13:00 | 44579.5417 | 11953.13
2022-01-18 14:00 | 44579.5833 | 11931.22
2022-01-18 15:00 | 44579.625 | 11969.31
2022-01-18 16:00 | 44579.6667 | 12493.29
2022-01-18 17:00 | 44579.7083 | 12612.96
2022-01-18 18:00 | 44579.75 | 12230.56
2022-01-18 19:00 | 44579.7917 | 11622.17
2022-01-18 20:00 | 44579.8333 | 11113.64
2022-01-18 21:00 | 44579.875 | 11302.73
2022-01-18 22:00 | 44579.9167 | 11210.56
2022-01-18 23:00 | 44579.9583 | 10533.29
2022-01-19 | 44580 | 9805.859
2022-01-19 01:00 | 44580.0417 | 9414.25
2022-01-19 02:00 | 44580.0833 | 9244.421
2022-01-19 03:00 | 44580.125 | 9255.605
2022-01-19 04:00 | 44580.1667 | 9715.376
2022-01-19 05:00 | 44580.2083 | 10732.3
2022-01-19 06:00 | 44580.25 | 11466.66
2022-01-19 07:00 | 44580.2917 | 11766.5
2022-01-19 08:00 | 44580.3333 | 11983.21
2022-01-19 09:00 | 44580.375 | 12080.51
2022-01-19 10:00 | 44580.4167 | 12170.83
2022-01-19 11:00 | 44580.4583 | 12034.01
2022-01-19 12:00 | 44580.5 | 12018.27
2022-01-19 13:00 | 44580.5417 | 11912.71
2022-01-19 14:00 | 44580.5833 | 11892.41
2022-01-19 15:00 | 44580.625 | 11929.73
2022-01-19 16:00 | 44580.6667 | 12464.45
2022-01-19 17:00 | 44580.7083 | 12585.39
2022-01-19 18:00 | 44580.75 | 12190.54
2022-01-19 19:00 | 44580.7917 | 11568.4
2022-01-19 20:00 | 44580.8333 | 11044.84
2022-01-19 21:00 | 44580.875 | 11245.37
2022-01-19 22:00 | 44580.9167 | 11166.53
2022-01-19 23:00 | 44580.9583 | 10485.33
2022-01-20 | 44581 | 9469.105
2022-01-20 01:00 | 44581.0417 | 9099.62
2022-01-20 02:00 | 44581.0833 | 8855.988
2022-01-20 03:00 | 44581.125 | 8764.1
2022-01-20 04:00 | 44581.1667 | 8757.244
2022-01-20 05:00 | 44581.2083 | 9130.837
2022-01-20 06:00 | 44581.25 | 9546.117
2022-01-20 07:00 | 44581.2917 | 9883.213
2022-01-20 08:00 | 44581.3333 | 10217.36
2022-01-20 09:00 | 44581.375 | 10392.76
2022-01-20 10:00 | 44581.4167 | 10614.07
2022-01-20 11:00 | 44581.4583 | 10497.74
2022-01-20 12:00 | 44581.5 | 10384.92
2022-01-20 13:00 | 44581.5417 | 10246.89
2022-01-20 14:00 | 44581.5833 | 10223.98
2022-01-20 15:00 | 44581.625 | 10273.97
2022-01-20 16:00 | 44581.6667 | 10801.34
2022-01-20 17:00 | 44581.7083 | 11078.37
2022-01-20 18:00 | 44581.75 | 10963.63
2022-01-20 19:00 | 44581.7917 | 10613.36
2022-01-20 20:00 | 44581.8333 | 10199.61
2022-01-20 21:00 | 44581.875 | 10406.17
2022-01-20 22:00 | 44581.9167 | 10419.23
2022-01-20 23:00 | 44581.9583 | 9908.001
2022-01-21 | 44582 | 9224.553
2022-01-21 01:00 | 44582.0417 | 8774.119
2022-01-21 02:00 | 44582.0833 | 8468.272
2022-01-21 03:00 | 44582.125 | 8283.871
2022-01-21 04:00 | 44582.1667 | 8151.39
2022-01-21 05:00 | 44582.2083 | 8319.123
2022-01-21 06:00 | 44582.25 | 8698.026
2022-01-21 07:00 | 44582.2917 | 9192.632
2022-01-21 08:00 | 44582.3333 | 9699.208
2022-01-21 09:00 | 44582.375 | 9990.875
2022-01-21 10:00 | 44582.4167 | 10308.3
2022-01-21 11:00 | 44582.4583 | 10152.68
2022-01-21 12:00 | 44582.5 | 9929.877
2022-01-21 13:00 | 44582.5417 | 9723.932
2022-01-21 14:00 | 44582.5833 | 9678.824
2022-01-21 15:00 | 44582.625 | 9758.891
2022-01-21 16:00 | 44582.6667 | 10389.6
2022-01-21 17:00 | 44582.7083 | 10815.8
2022-01-21 18:00 | 44582.75 | 10816
2022-01-21 19:00 | 44582.7917 | 10547.82
2022-01-21 20:00 | 44582.8333 | 10138.42
2022-01-21 21:00 | 44582.875 | 10328.55
2022-01-21 22:00 | 44582.9167 | 10272.18
2022-01-21 23:00 | 44582.9583 | 9668.116
2022-01-22 | 44583 | 9794.353
2022-01-22 01:00 | 44583.0417 | 9403.199
2022-01-22 02:00 | 44583.0833 | 9234.036
2022-01-22 03:00 | 44583.125 | 9247.001
2022-01-22 04:00 | 44583.1667 | 9701.621
2022-01-22 05:00 | 44583.2083 | 10709.23
2022-01-22 06:00 | 44583.25 | 11439.39
2022-01-22 07:00 | 44583.2917 | 11743.47
2022-01-22 08:00 | 44583.3333 | 11964.02
2022-01-22 09:00 | 44583.375 | 12065.15
2022-01-22 10:00 | 44583.4167 | 12155.49
2022-01-22 11:00 | 44583.4583 | 12017.59
2022-01-22 12:00 | 44583.5 | 11997.9
2022-01-22 13:00 | 44583.5417 | 11890.2
2022-01-22 14:00 | 44583.5833 | 11869.05
2022-01-22 15:00 | 44583.625 | 11907.46
2022-01-22 16:00 | 44583.6667 | 12439.59
2022-01-22 17:00 | 44583.7083 | 12562.25
2022-01-22 18:00 | 44583.75 | 12174.58
2022-01-22 19:00 | 44583.7917 | 11559.26
2022-01-22 20:00 | 44583.8333 | 11042.1
2022-01-22 21:00 | 44583.875 | 11237.6
2022-01-22 22:00 | 44583.9167 | 11152.09
2022-01-22 23:00 | 44583.9583 | 10471.12
2022-01-23 | 44584 | 9854.455
2022-01-23 01:00 | 44584.0417 | 9466.187
2022-01-23 02:00 | 44584.0833 | 9298.243
2022-01-23 03:00 | 44584.125 | 9310.596
2022-01-23 04:00 | 44584.1667 | 9761.961
2022-01-23 05:00 | 44584.2083 | 10764.52
2022-01-23 06:00 | 44584.25 | 11490.06
2022-01-23 07:00 | 44584.2917 | 11789.84
2022-01-23 08:00 | 44584.3333 | 12007.14
2022-01-23 09:00 | 44584.375 | 12106.11
2022-01-23 10:00 | 44584.4167 | 12195.66
2022-01-23 11:00 | 44584.4583 | 12059.29
2022-01-23 12:00 | 44584.5 | 12041.35
2022-01-23 13:00 | 44584.5417 | 11934.95
2022-01-23 14:00 | 44584.5833 | 11914.52
2022-01-23 15:00 | 44584.625 | 11952.29
2022-01-23 16:00 | 44584.6667 | 12481.65
2022-01-23 17:00 | 44584.7083 | 12602.27
2022-01-23 18:00 | 44584.75 | 12215.36
2022-01-23 19:00 | 44584.7917 | 11602.5
2022-01-23 20:00 | 44584.8333 | 11086.88
2022-01-23 21:00 | 44584.875 | 11283.21
2022-01-23 22:00 | 44584.9167 | 11201.77
2022-01-23 23:00 | 44584.9583 | 10526.64
2022-01-24 | 44585 | 9922.936
2022-01-24 01:00 | 44585.0417 | 9541.298
2022-01-24 02:00 | 44585.0833 | 9378.938
2022-01-24 03:00 | 44585.125 | 9391.722
2022-01-24 04:00 | 44585.1667 | 9838.199
2022-01-24 05:00 | 44585.2083 | 10809.46
2022-01-24 06:00 | 44585.25 | 11517.36
2022-01-24 07:00 | 44585.2917 | 11825.52
2022-01-24 08:00 | 44585.3333 | 12049.1
2022-01-24 09:00 | 44585.375 | 12155.92
2022-01-24 10:00 | 44585.4167 | 12241.62
2022-01-24 11:00 | 44585.4583 | 12103.28
2022-01-24 12:00 | 44585.5 | 12074.94
2022-01-24 13:00 | 44585.5417 | 11966.24
2022-01-24 14:00 | 44585.5833 | 11943.1
2022-01-24 15:00 | 44585.625 | 11982.74
2022-01-24 16:00 | 44585.6667 | 12494.22
2022-01-24 17:00 | 44585.7083 | 12614.62
2022-01-24 18:00 | 44585.75 | 12251.39
2022-01-24 19:00 | 44585.7917 | 11664.12
2022-01-24 20:00 | 44585.8333 | 11175
2022-01-24 21:00 | 44585.875 | 11351.73
2022-01-24 22:00 | 44585.9167 | 11247.74
2022-01-24 23:00 | 44585.9583 | 10580
2022-01-25 | 44586 | 9904.921
2022-01-25 01:00 | 44586.0417 | 9518.986
2022-01-25 02:00 | 44586.0833 | 9353.051
2022-01-25 03:00 | 44586.125 | 9364.712
2022-01-25 04:00 | 44586.1667 | 9810.015
2022-01-25 05:00 | 44586.2083 | 10791.9
2022-01-25 06:00 | 44586.25 | 11507.03
2022-01-25 07:00 | 44586.2917 | 11813.91
2022-01-25 08:00 | 44586.3333 | 12037.46
2022-01-25 09:00 | 44586.375 | 12142.49
2022-01-25 10:00 | 44586.4167 | 12231.59
2022-01-25 11:00 | 44586.4583 | 12093.45
2022-01-25 12:00 | 44586.5 | 12067.95
2022-01-25 13:00 | 44586.5417 | 11959.56
2022-01-25 14:00 | 44586.5833 | 11937.33
2022-01-25 15:00 | 44586.625 | 11976.61
2022-01-25 16:00 | 44586.6667 | 12497.41
2022-01-25 17:00 | 44586.7083 | 12620.43
2022-01-25 18:00 | 44586.75 | 12248.71
2022-01-25 19:00 | 44586.7917 | 11651.15
2022-01-25 20:00 | 44586.8333 | 11150.2
2022-01-25 21:00 | 44586.875 | 11335.49
2022-01-25 22:00 | 44586.9167 | 11240.56
2022-01-25 23:00 | 44586.9583 | 10568.07
2022-01-26 | 44587 | 9929.062
2022-01-26 01:00 | 44587.0417 | 9540.252
2022-01-26 02:00 | 44587.0833 | 9371.677
2022-01-26 03:00 | 44587.125 | 9382.357
2022-01-26 04:00 | 44587.1667 | 9828.876
2022-01-26 05:00 | 44587.2083 | 10819.19
2022-01-26 06:00 | 44587.25 | 11539.83
2022-01-26 07:00 | 44587.2917 | 11845.77
2022-01-26 08:00 | 44587.3333 | 12069.1
2022-01-26 09:00 | 44587.375 | 12173.02
2022-01-26 10:00 | 44587.4167 | 12263.75
2022-01-26 11:00 | 44587.4583 | 12125.72
2022-01-26 12:00 | 44587.5 | 12102.33
2022-01-26 13:00 | 44587.5417 | 11994.66
2022-01-26 14:00 | 44587.5833 | 11973.04
2022-01-26 15:00 | 44587.625 | 12012.04
2022-01-26 16:00 | 44587.6667 | 12539.22
2022-01-26 17:00 | 44587.7083 | 12663.62
2022-01-26 18:00 | 44587.75 | 12285.67
2022-01-26 19:00 | 44587.7917 | 11680.68
2022-01-26 20:00 | 44587.8333 | 11171.55
2022-01-26 21:00 | 44587.875 | 11362.61
2022-01-26 22:00 | 44587.9167 | 11273.73
2022-01-26 23:00 | 44587.9583 | 10597.84
2022-01-27 | 44588 | 9596.419
2022-01-27 01:00 | 44588.0417 | 9234.95
2022-01-27 02:00 | 44588.0833 | 8999.305
2022-01-27 03:00 | 44588.125 | 8913.421
2022-01-27 04:00 | 44588.1667 | 8902.348
2022-01-27 05:00 | 44588.2083 | 9241.757
2022-01-27 06:00 | 44588.25 | 9637.832
2022-01-27 07:00 | 44588.2917 | 9987.488
2022-01-27 08:00 | 44588.3333 | 10330.18
2022-01-27 09:00 | 44588.375 | 10516.88
2022-01-27 10:00 | 44588.4167 | 10730.65
2022-01-27 11:00 | 44588.4583 | 10610.5
2022-01-27 12:00 | 44588.5 | 10483.68
2022-01-27 13:00 | 44588.5417 | 10342.16
2022-01-27 14:00 | 44588.5833 | 10315.55
2022-01-27 15:00 | 44588.625 | 10368.48
2022-01-27 16:00 | 44588.6667 | 10872.69
2022-01-27 17:00 | 44588.7083 | 11147.69
2022-01-27 18:00 | 44588.75 | 11062.15
2022-01-27 19:00 | 44588.7917 | 10743.29
2022-01-27 20:00 | 44588.8333 | 10364.36
2022-01-27 21:00 | 44588.875 | 10543.42
2022-01-27 22:00 | 44588.9167 | 10522.81
2022-01-27 23:00 | 44588.9583 | 10017.83
2022-01-28 | 44589 | 9248.236
2022-01-28 01:00 | 44589.0417 | 8797.3
2022-01-28 02:00 | 44589.0833 | 8493.878
2022-01-28 03:00 | 44589.125 | 8314.999
2022-01-28 04:00 | 44589.1667 | 8184.883
2022-01-28 05:00 | 44589.2083 | 8340.586
2022-01-28 06:00 | 44589.25 | 8715.657
2022-01-28 07:00 | 44589.2917 | 9226.38
2022-01-28 08:00 | 44589.3333 | 9744.79
2022-01-28 09:00 | 44589.375 | 10047.99
2022-01-28 10:00 | 44589.4167 | 10361.91
2022-01-28 11:00 | 44589.4583 | 10200.76
2022-01-28 12:00 | 44589.5 | 9965.7
2022-01-28 13:00 | 44589.5417 | 9755.012
2022-01-28 14:00 | 44589.5833 | 9706.29
2022-01-28 15:00 | 44589.625 | 9789.632
2022-01-28 16:00 | 44589.6667 | 10411.97
2022-01-28 17:00 | 44589.7083 | 10844.9
2022-01-28 18:00 | 44589.75 | 10851.36
2022-01-28 19:00 | 44589.7917 | 10604.45
2022-01-28 20:00 | 44589.8333 | 10213.78
2022-01-28 21:00 | 44589.875 | 10385.25
2022-01-28 22:00 | 44589.9167 | 10300.28
2022-01-28 23:00 | 44589.9583 | 9689.004
2022-01-29 | 44590 | 9822.79
2022-01-29 01:00 | 44590.0417 | 9440.464
2022-01-29 02:00 | 44590.0833 | 9279.209
2022-01-29 03:00 | 44590.125 | 9296.909
2022-01-29 04:00 | 44590.1667 | 9753.243
2022-01-29 05:00 | 44590.2083 | 10736.31
2022-01-29 06:00 | 44590.25 | 11450.74
2022-01-29 07:00 | 44590.2917 | 11760.75
2022-01-29 08:00 | 44590.3333 | 11983.86
2022-01-29 09:00 | 44590.375 | 12090.99
2022-01-29 10:00 | 44590.4167 | 12172.87
2022-01-29 11:00 | 44590.4583 | 12032.94
2022-01-29 12:00 | 44590.5 | 12004.66
2022-01-29 13:00 | 44590.5417 | 11896.9
2022-01-29 14:00 | 44590.5833 | 11873.22
2022-01-29 15:00 | 44590.625 | 11913.09
2022-01-29 16:00 | 44590.6667 | 12423.32
2022-01-29 17:00 | 44590.7083 | 12540.64
2022-01-29 18:00 | 44590.75 | 12173.85
2022-01-29 19:00 | 44590.7917 | 11582.89
2022-01-29 20:00 | 44590.8333 | 11094.18
2022-01-29 21:00 | 44590.875 | 11267.88
2022-01-29 22:00 | 44590.9167 | 11157.32
2022-01-29 23:00 | 44590.9583 | 10484.51
2022-01-30 | 44591 | 9905.326
2022-01-30 01:00 | 44591.0417 | 9532.491
2022-01-30 02:00 | 44591.0833 | 9378.457
2022-01-30 03:00 | 44591.125 | 9397.309
2022-01-30 04:00 | 44591.1667 | 9845.183
2022-01-30 05:00 | 44591.2083 | 10789.22
2022-01-30 06:00 | 44591.25 | 11480.51
2022-01-30 07:00 | 44591.2917 | 11797.42
2022-01-30 08:00 | 44591.3333 | 12025.66
2022-01-30 09:00 | 44591.375 | 12140.56
2022-01-30 10:00 | 44591.4167 | 12217.02
2022-01-30 11:00 | 44591.4583 | 12075.73
2022-01-30 12:00 | 44591.5 | 12036.63
2022-01-30 13:00 | 44591.5417 | 11927.59
2022-01-30 14:00 | 44591.5833 | 11901.33
2022-01-30 15:00 | 44591.625 | 11943
2022-01-30 16:00 | 44591.6667 | 12430.82
2022-01-30 17:00 | 44591.7083 | 12546.23
2022-01-30 18:00 | 44591.75 | 12207.09
2022-01-30 19:00 | 44591.7917 | 11647.07
2022-01-30 20:00 | 44591.8333 | 11189.82
2022-01-30 21:00 | 44591.875 | 11341.42
2022-01-30 22:00 | 44591.9167 | 11207.39
2022-01-30 23:00 | 44591.9583 | 10546.78
2022-01-31 | 44592 | 9921.619
2022-01-31 01:00 | 44592.0417 | 9551.341
2022-01-31 02:00 | 44592.0833 | 9397.891
2022-01-31 03:00 | 44592.125 | 9414.308
2022-01-31 04:00 | 44592.1667 | 9854.841
2022-01-31 05:00 | 44592.2083 | 10788.15
2022-01-31 06:00 | 44592.25 | 11472.26
2022-01-31 07:00 | 44592.2917 | 11785.93
2022-01-31 08:00 | 44592.3333 | 12012.66
2022-01-31 09:00 | 44592.375 | 12126.7
2022-01-31 10:00 | 44592.4167 | 12204.17
2022-01-31 11:00 | 44592.4583 | 12064.47
2022-01-31 12:00 | 44592.5 | 12025.83
2022-01-31 13:00 | 44592.5417 | 11916.61
2022-01-31 14:00 | 44592.5833 | 11890.9
2022-01-31 15:00 | 44592.625 | 11932.15
2022-01-31 16:00 | 44592.6667 | 12417.55
2022-01-31 17:00 | 44592.7083 | 12533.34
2022-01-31 18:00 | 44592.75 | 12197.72
2022-01-31 19:00 | 44592.7917 | 11642.5
2022-01-31 20:00 | 44592.8333 | 11187.61
2022-01-31 21:00 | 44592.875 | 11339.97
2022-01-31 22:00 | 44592.9167 | 11210.3
2022-01-31 23:00 | 44592.9583 | 10556.32
2022-02-01 | 44593 | 9941.492
2022-02-01 01:00 | 44593.0417 | 9566.911
2022-02-01 02:00 | 44593.0833 | 9410.336
2022-02-01 03:00 | 44593.125 | 9426.834
2022-02-01 04:00 | 44593.1667 | 9876.022
2022-02-01 05:00 | 44593.2083 | 10833.27
2022-02-01 06:00 | 44593.25 | 11530.8
2022-02-01 07:00 | 44593.2917 | 11839.95
2022-02-01 08:00 | 44593.3333 | 12062.51
2022-02-01 09:00 | 44593.375 | 12171.37
2022-02-01 10:00 | 44593.4167 | 12250.06
2022-02-01 11:00 | 44593.4583 | 12111.1
2022-02-01 12:00 | 44593.5 | 12079.02
2022-02-01 13:00 | 44593.5417 | 11971.73
2022-02-01 14:00 | 44593.5833 | 11947.51
2022-02-01 15:00 | 44593.625 | 11987.63
2022-02-01 16:00 | 44593.6667 | 12483.38
2022-02-01 17:00 | 44593.7083 | 12598.14
2022-02-01 18:00 | 44593.75 | 12246.51
2022-02-01 19:00 | 44593.7917 | 11674.09
2022-02-01 20:00 | 44593.8333 | 11203.02
2022-02-01 21:00 | 44593.875 | 11366.39
2022-02-01 22:00 | 44593.9167 | 11248.23
2022-02-01 23:00 | 44593.9583 | 10587.81
2022-02-02 | 44594 | 9919.679
2022-02-02 01:00 | 44594.0417 | 9545.35
2022-02-02 02:00 | 44594.0833 | 9389.455
2022-02-02 03:00 | 44594.125 | 9405.648
2022-02-02 04:00 | 44594.1667 | 9854.107
2022-02-02 05:00 | 44594.2083 | 10805.9
2022-02-02 06:00 | 44594.25 | 11501.09
2022-02-02 07:00 | 44594.2917 | 11813.49
2022-02-02 08:00 | 44594.3333 | 12038.69
2022-02-02 09:00 | 44594.375 | 12150.07
2022-02-02 10:00 | 44594.4167 | 12228.37
2022-02-02 11:00 | 44594.4583 | 12088.36
2022-02-02 12:00 | 44594.5 | 12053.39
2022-02-02 13:00 | 44594.5417 | 11945.55
2022-02-02 14:00 | 44594.5833 | 11920.69
2022-02-02 15:00 | 44594.625 | 11961.6
2022-02-02 16:00 | 44594.6667 | 12454.98
2022-02-02 17:00 | 44594.7083 | 12570.46
2022-02-02 18:00 | 44594.75 | 12223.58
2022-02-02 19:00 | 44594.7917 | 11655.67
2022-02-02 20:00 | 44594.8333 | 11189.25
2022-02-02 21:00 | 44594.875 | 11348.63
2022-02-02 22:00 | 44594.9167 | 11224.95
2022-02-02 23:00 | 44594.9583 | 10564.18
2022-02-03 | 44595 | 9538.86
2022-02-03 01:00 | 44595.0417 | 9178.438
2022-02-03 02:00 | 44595.0833 | 8945.87
2022-02-03 03:00 | 44595.125 | 8863.019
2022-02-03 04:00 | 44595.1667 | 8858.389
2022-02-03 05:00 | 44595.2083 | 9185.762
2022-02-03 06:00 | 44595.25 | 9577.671
2022-02-03 07:00 | 44595.2917 | 9939.831
2022-02-03 08:00 | 44595.3333 | 10291.24
2022-02-03 09:00 | 44595.375 | 10487.2
2022-02-03 10:00 | 44595.4167 | 10696.41
2022-02-03 11:00 | 44595.4583 | 10571.93
2022-02-03 12:00 | 44595.5 | 10435.18
2022-02-03 13:00 | 44595.5417 | 10290.08
2022-02-03 14:00 | 44595.5833 | 10260.43
2022-02-03 15:00 | 44595.625 | 10316.01
2022-02-03 16:00 | 44595.6667 | 10810.73
2022-02-03 17:00 | 44595.7083 | 11085.92
2022-02-03 18:00 | 44595.75 | 11015.2
2022-02-03 19:00 | 44595.7917 | 10710.5
2022-02-03 20:00 | 44595.8333 | 10349.54
2022-02-03 21:00 | 44595.875 | 10511.49
2022-02-03 22:00 | 44595.9167 | 10465.83
2022-02-03 23:00 | 44595.9583 | 9956.59
2022-02-04 | 44596 | 9223.814
2022-02-04 01:00 | 44596.0417 | 8777.966
2022-02-04 02:00 | 44596.0833 | 8477.979
2022-02-04 03:00 | 44596.125 | 8291.302
2022-02-04 04:00 | 44596.1667 | 8157.781
2022-02-04 05:00 | 44596.2083 | 8288.688
2022-02-04 06:00 | 44596.25 | 8651.671
2022-02-04 07:00 | 44596.2917 | 9164.089
2022-02-04 08:00 | 44596.3333 | 9684.694
2022-02-04 09:00 | 44596.375 | 9991.232
2022-02-04 10:00 | 44596.4167 | 10303.62
2022-02-04 11:00 | 44596.4583 | 10142.46
2022-02-04 12:00 | 44596.5 | 9902.531
2022-02-04 13:00 | 44596.5417 | 9691.443
2022-02-04 14:00 | 44596.5833 | 9642.07
2022-02-04 15:00 | 44596.625 | 9726.232
2022-02-04 16:00 | 44596.6667 | 10338.2
2022-02-04 17:00 | 44596.7083 | 10780.48
2022-02-04 18:00 | 44596.75 | 10787.32
2022-02-04 19:00 | 44596.7917 | 10560.99
2022-02-04 20:00 | 44596.8333 | 10184.87
2022-02-04 21:00 | 44596.875 | 10347.59
2022-02-04 22:00 | 44596.9167 | 10255.15
2022-02-04 23:00 | 44596.9583 | 9652.442
2022-02-05 | 44597 | 9739.393
2022-02-05 01:00 | 44597.0417 | 9363.931
2022-02-05 02:00 | 44597.0833 | 9209.94
2022-02-05 03:00 | 44597.125 | 9234.083
2022-02-05 04:00 | 44597.1667 | 9690.632
2022-02-05 05:00 | 44597.2083 | 10643.39
2022-02-05 06:00 | 44597.25 | 11341.48
2022-02-05 07:00 | 44597.2917 | 11665.83
2022-02-05 08:00 | 44597.3333 | 11898.48
2022-02-05 09:00 | 44597.375 | 12017.55
2022-02-05 10:00 | 44597.4167 | 12091.55
2022-02-05 11:00 | 44597.4583 | 11947.09
2022-02-05 12:00 | 44597.5 | 11904.43
2022-02-05 13:00 | 44597.5417 | 11792.94
2022-02-05 14:00 | 44597.5833 | 11765.28
2022-02-05 15:00 | 44597.625 | 11808.35
2022-02-05 16:00 | 44597.6667 | 12296.03
2022-02-05 17:00 | 44597.7083 | 12411.26
2022-02-05 18:00 | 44597.75 | 12072.57
2022-02-05 19:00 | 44597.7917 | 11511.34
2022-02-05 20:00 | 44597.8333 | 11056.95
2022-02-05 21:00 | 44597.875 | 11202.2
2022-02-05 22:00 | 44597.9167 | 11055.22
2022-02-05 23:00 | 44597.9583 | 10385.66
2022-02-06 | 44598 | 9736.5
2022-02-06 01:00 | 44598.0417 | 9356.386
2022-02-06 02:00 | 44598.0833 | 9199.317
2022-02-06 03:00 | 44598.125 | 9220.055
2022-02-06 04:00 | 44598.1667 | 9685.315
2022-02-06 05:00 | 44598.2083 | 10658.64
2022-02-06 06:00 | 44598.25 | 11368.89
2022-02-06 07:00 | 44598.2917 | 11690.1
2022-02-06 08:00 | 44598.3333 | 11920.25
2022-02-06 09:00 | 44598.375 | 12035.63
2022-02-06 10:00 | 44598.4167 | 12111.91
2022-02-06 11:00 | 44598.4583 | 11968.01
2022-02-06 12:00 | 44598.5 | 11930.63
2022-02-06 13:00 | 44598.5417 | 11819.23
2022-02-06 14:00 | 44598.5833 | 11792.92
2022-02-06 15:00 | 44598.625 | 11835.41
2022-02-06 16:00 | 44598.6667 | 12334.3
2022-02-06 17:00 | 44598.7083 | 12450
2022-02-06 18:00 | 44598.75 | 12097.34
2022-02-06 19:00 | 44598.7917 | 11520.58
2022-02-06 20:00 | 44598.8333 | 11050.86
2022-02-06 21:00 | 44598.875 | 11206.65
2022-02-06 22:00 | 44598.9167 | 11070.49
2022-02-06 23:00 | 44598.9583 | 10394.44
2022-02-07 | 44599 | 9827.136
2022-02-07 01:00 | 44599.0417 | 9454.622
2022-02-07 02:00 | 44599.0833 | 9300.935
2022-02-07 03:00 | 44599.125 | 9323.689
2022-02-07 04:00 | 44599.1667 | 9772.937
2022-02-07 05:00 | 44599.2083 | 10718.61
2022-02-07 06:00 | 44599.25 | 11410.75
2022-02-07 07:00 | 44599.2917 | 11728.85
2022-02-07 08:00 | 44599.3333 | 11957.62
2022-02-07 09:00 | 44599.375 | 12073.74
2022-02-07 10:00 | 44599.4167 | 12148.41
2022-02-07 11:00 | 44599.4583 | 12006.49
2022-02-07 12:00 | 44599.5 | 11966.69
2022-02-07 13:00 | 44599.5417 | 11856.01
2022-02-07 14:00 | 44599.5833 | 11829.63
2022-02-07 15:00 | 44599.625 | 11871.86
2022-02-07 16:00 | 44599.6667 | 12358.39
2022-02-07 17:00 | 44599.7083 | 12472.77
2022-02-07 18:00 | 44599.75 | 12134.1
2022-02-07 19:00 | 44599.7917 | 11574.72
2022-02-07 20:00 | 44599.8333 | 11119.61
2022-02-07 21:00 | 44599.875 | 11268.65
2022-02-07 22:00 | 44599.9167 | 11130.62
2022-02-07 23:00 | 44599.9583 | 10468.83
2022-02-08 | 44600 | 9847.461
2022-02-08 01:00 | 44600.0417 | 9472.177
2022-02-08 02:00 | 44600.0833 | 9315.511
2022-02-08 03:00 | 44600.125 | 9334.224
2022-02-08 04:00 | 44600.1667 | 9775.08
2022-02-08 05:00 | 44600.2083 | 10715.25
2022-02-08 06:00 | 44600.25 | 11406.42
2022-02-08 07:00 | 44600.2917 | 11726.68
2022-02-08 08:00 | 44600.3333 | 11959.35
2022-02-08 09:00 | 44600.375 | 12077.18
2022-02-08 10:00 | 44600.4167 | 12156.27
2022-02-08 11:00 | 44600.4583 | 12014.08
2022-02-08 12:00 | 44600.5 | 11972.75
2022-02-08 13:00 | 44600.5417 | 11861.55
2022-02-08 14:00 | 44600.5833 | 11835.2
2022-02-08 15:00 | 44600.625 | 11877.83
2022-02-08 16:00 | 44600.6667 | 12370.13
2022-02-08 17:00 | 44600.7083 | 12489.67
2022-02-08 18:00 | 44600.75 | 12152.37
2022-02-08 19:00 | 44600.7917 | 11592.63
2022-02-08 20:00 | 44600.8333 | 11133.5
2022-02-08 21:00 | 44600.875 | 11286.42
2022-02-08 22:00 | 44600.9167 | 11152.85
2022-02-08 23:00 | 44600.9583 | 10489.73
2022-02-09 | 44601 | 9915.209
2022-02-09 01:00 | 44601.0417 | 9543.479
2022-02-09 02:00 | 44601.0833 | 9389.261
2022-02-09 03:00 | 44601.125 | 9405.728
2022-02-09 04:00 | 44601.1667 | 9838.8
2022-02-09 05:00 | 44601.2083 | 10756.7
2022-02-09 06:00 | 44601.25 | 11435.46
2022-02-09 07:00 | 44601.2917 | 11759.24
2022-02-09 08:00 | 44601.3333 | 11995.71
2022-02-09 09:00 | 44601.375 | 12117.83
2022-02-09 10:00 | 44601.4167 | 12196.43
2022-02-09 11:00 | 44601.4583 | 12053.7
2022-02-09 12:00 | 44601.5 | 12006.79
2022-02-09 13:00 | 44601.5417 | 11893.83
2022-02-09 14:00 | 44601.5833 | 11866.73
2022-02-09 15:00 | 44601.625 | 11910.37
2022-02-09 16:00 | 44601.6667 | 12394.37
2022-02-09 17:00 | 44601.7083 | 12515.22
2022-02-09 18:00 | 44601.75 | 12191.91
2022-02-09 19:00 | 44601.7917 | 11647.2
2022-02-09 20:00 | 44601.8333 | 11201.46
2022-02-09 21:00 | 44601.875 | 11345.77
2022-02-09 22:00 | 44601.9167 | 11203.75
2022-02-09 23:00 | 44601.9583 | 10546.77
2022-02-10 | 44602 | 9566.768
2022-02-10 01:00 | 44602.0417 | 9210.844
2022-02-10 02:00 | 44602.0833 | 8981.438
2022-02-10 03:00 | 44602.125 | 8899.908
2022-02-10 04:00 | 44602.1667 | 8890.687
2022-02-10 05:00 | 44602.2083 | 9205.28
2022-02-10 06:00 | 44602.25 | 9588.316
2022-02-10 07:00 | 44602.2917 | 9949.741
2022-02-10 08:00 | 44602.3333 | 10300.59
2022-02-10 09:00 | 44602.375 | 10497.53
2022-02-10 10:00 | 44602.4167 | 10704.01
2022-02-10 11:00 | 44602.4583 | 10579.92
2022-02-10 12:00 | 44602.5 | 10441.3
2022-02-10 13:00 | 44602.5417 | 10296.07
2022-02-10 14:00 | 44602.5833 | 10266.3
2022-02-10 15:00 | 44602.625 | 10322.17
2022-02-10 16:00 | 44602.6667 | 10809.02
2022-02-10 17:00 | 44602.7083 | 11081.87
2022-02-10 18:00 | 44602.75 | 11018.82
2022-02-10 19:00 | 44602.7917 | 10724.13
2022-02-10 20:00 | 44602.8333 | 10373.18
2022-02-10 21:00 | 44602.875 | 10529.08
2022-02-10 22:00 | 44602.9167 | 10478.69
2022-02-10 23:00 | 44602.9583 | 9976.204
2022-02-11 | 44603 | 9225.998
2022-02-11 01:00 | 44603.0417 | 8780.482
2022-02-11 02:00 | 44603.0833 | 8483.138
2022-02-11 03:00 | 44603.125 | 8303.644
2022-02-11 04:00 | 44603.1667 | 8178.683
2022-02-11 05:00 | 44603.2083 | 8310.103
2022-02-11 06:00 | 44603.25 | 8672.184
2022-02-11 07:00 | 44603.2917 | 9195.156
2022-02-11 08:00 | 44603.3333 | 9722.164
2022-02-11 09:00 | 44603.375 | 10035.82
2022-02-11 10:00 | 44603.4167 | 10342.8
2022-02-11 11:00 | 44603.4583 | 10177.55
2022-02-11 12:00 | 44603.5 | 9930.253
2022-02-11 13:00 | 44603.5417 | 9715.944
2022-02-11 14:00 | 44603.5833 | 9663.965
2022-02-11 15:00 | 44603.625 | 9750.282
2022-02-11 16:00 | 44603.6667 | 10355.02
2022-02-11 17:00 | 44603.7083 | 10798.09
2022-02-11 18:00 | 44603.75 | 10809.93
2022-02-11 19:00 | 44603.7917 | 10593.55
2022-02-11 20:00 | 44603.8333 | 10231.07
2022-02-11 21:00 | 44603.875 | 10379.22
2022-02-11 22:00 | 44603.9167 | 10264.09
2022-02-11 23:00 | 44603.9583 | 9655.053
2022-02-12 | 44604 | 9903.422
2022-02-12 01:00 | 44604.0417 | 9537.286
2022-02-12 02:00 | 44604.0833 | 9388.567
2022-02-12 03:00 | 44604.125 | 9409.533
2022-02-12 04:00 | 44604.1667 | 9846.771
2022-02-12 05:00 | 44604.2083 | 10754.87
2022-02-12 06:00 | 44604.25 | 11426.29
2022-02-12 07:00 | 44604.2917 | 11752.39
2022-02-12 08:00 | 44604.3333 | 11988.63
2022-02-12 09:00 | 44604.375 | 12113.08
2022-02-12 10:00 | 44604.4167 | 12185.31
2022-02-12 11:00 | 44604.4583 | 12041.59
2022-02-12 12:00 | 44604.5 | 11990.84
2022-02-12 13:00 | 44604.5417 | 11878.61
2022-02-12 14:00 | 44604.5833 | 11849.84
2022-02-12 15:00 | 44604.625 | 11893.98
2022-02-12 16:00 | 44604.6667 | 12364.61
2022-02-12 17:00 | 44604.7083 | 12480.59
2022-02-12 18:00 | 44604.75 | 12167.27
2022-02-12 19:00 | 44604.7917 | 11635.03
2022-02-12 20:00 | 44604.8333 | 11205.48
2022-02-12 21:00 | 44604.875 | 11336.99
2022-02-12 22:00 | 44604.9167 | 11180.1
2022-02-12 23:00 | 44604.9583 | 10527.63
2022-02-13 | 44605 | 9973.327
2022-02-13 01:00 | 44605.0417 | 9609.015
2022-02-13 02:00 | 44605.0833 | 9459.259
2022-02-13 03:00 | 44605.125 | 9476.378
2022-02-13 04:00 | 44605.1667 | 9903.633
2022-02-13 05:00 | 44605.2083 | 10806.78
2022-02-13 06:00 | 44605.25 | 11473.4
2022-02-13 07:00 | 44605.2917 | 11790.57
2022-02-13 08:00 | 44605.3333 | 12021.66
2022-02-13 09:00 | 44605.375 | 12141.23
2022-02-13 10:00 | 44605.4167 | 12216.18
2022-02-13 11:00 | 44605.4583 | 12075.92
2022-02-13 12:00 | 44605.5 | 12030.22
2022-02-13 13:00 | 44605.5417 | 11919.48
2022-02-13 14:00 | 44605.5833 | 11892.67
2022-02-13 15:00 | 44605.625 | 11935.37
2022-02-13 16:00 | 44605.6667 | 12408.95
2022-02-13 17:00 | 44605.7083 | 12525.06
2022-02-13 18:00 | 44605.75 | 12207.93
2022-02-13 19:00 | 44605.7917 | 11673.45
2022-02-13 20:00 | 44605.8333 | 11237.39
2022-02-13 21:00 | 44605.875 | 11377.95
2022-02-13 22:00 | 44605.9167 | 11237.34
2022-02-13 23:00 | 44605.9583 | 10593.17
2022-02-14 | 44606 | 9984.847
2022-02-14 01:00 | 44606.0417 | 9619.221
2022-02-14 02:00 | 44606.0833 | 9468.641
2022-02-14 03:00 | 44606.125 | 9484.767
2022-02-14 04:00 | 44606.1667 | 9913.165
2022-02-14 05:00 | 44606.2083 | 10818.63
2022-02-14 06:00 | 44606.25 | 11487.2
2022-02-14 07:00 | 44606.2917 | 11805.27
2022-02-14 08:00 | 44606.3333 | 12037.29
2022-02-14 09:00 | 44606.375 | 12157.13
2022-02-14 10:00 | 44606.4167 | 12232.67
2022-02-14 11:00 | 44606.4583 | 12092.09
2022-02-14 12:00 | 44606.5 | 12046.43
2022-02-14 13:00 | 44606.5417 | 11935.38
2022-02-14 14:00 | 44606.5833 | 11908.6
2022-02-14 15:00 | 44606.625 | 11951.45
2022-02-14 16:00 | 44606.6667 | 12427.25
2022-02-14 17:00 | 44606.7083 | 12544.15
2022-02-14 18:00 | 44606.75 | 12225.74
2022-02-14 19:00 | 44606.7917 | 11689.38
2022-02-14 20:00 | 44606.8333 | 11251.32
2022-02-14 21:00 | 44606.875 | 11392.9
2022-02-14 22:00 | 44606.9167 | 11252.65
2022-02-14 23:00 | 44606.9583 | 10606.45
2022-02-15 | 44607 | 9926.922
2022-02-15 01:00 | 44607.0417 | 9562.875
2022-02-15 02:00 | 44607.0833 | 9415.614
2022-02-15 03:00 | 44607.125 | 9436.283
2022-02-15 04:00 | 44607.1667 | 9867.443
2022-02-15 05:00 | 44607.2083 | 10760.43
2022-02-15 06:00 | 44607.25 | 11423.78
2022-02-15 07:00 | 44607.2917 | 11753.35
2022-02-15 08:00 | 44607.3333 | 11993.05
2022-02-15 09:00 | 44607.375 | 12121.05
2022-02-15 10:00 | 44607.4167 | 12192.94
2022-02-15 11:00 | 44607.4583 | 12048.53
2022-02-15 12:00 | 44607.5 | 11993.34
2022-02-15 13:00 | 44607.5417 | 11879.66
2022-02-15 14:00 | 44607.5833 | 11849.98
2022-02-15 15:00 | 44607.625 | 11895
2022-02-15 16:00 | 44607.6667 | 12360.29
2022-02-15 17:00 | 44607.7083 | 12477.29
2022-02-15 18:00 | 44607.75 | 12173.91
2022-02-15 19:00 | 44607.7917 | 11652.18
2022-02-15 20:00 | 44607.8333 | 11232.23
2022-02-15 21:00 | 44607.875 | 11357.15
2022-02-15 22:00 | 44607.9167 | 11193.09
2022-02-15 23:00 | 44607.9583 | 10543.96
2022-02-16 | 44608 | 9957.697
2022-02-16 01:00 | 44608.0417 | 9605.462
2022-02-16 02:00 | 44608.0833 | 9465.987
2022-02-16 03:00 | 44608.125 | 9486.76
2022-02-16 04:00 | 44608.1667 | 9905.112
2022-02-16 05:00 | 44608.2083 | 10755.33
2022-02-16 06:00 | 44608.25 | 11391.67
2022-02-16 07:00 | 44608.2917 | 11722.86
2022-02-16 08:00 | 44608.3333 | 11964.03
2022-02-16 09:00 | 44608.375 | 12097.01
2022-02-16 10:00 | 44608.4167 | 12163.72
2022-02-16 11:00 | 44608.4583 | 12019.89
2022-02-16 12:00 | 44608.5 | 11956.53
2022-02-16 13:00 | 44608.5417 | 11842.37
2022-02-16 14:00 | 44608.5833 | 11811.02
2022-02-16 15:00 | 44608.625 | 11856.93
2022-02-16 16:00 | 44608.6667 | 12298.88
2022-02-16 17:00 | 44608.7083 | 12412.89
2022-02-16 18:00 | 44608.75 | 12136.3
2022-02-16 19:00 | 44608.7917 | 11646.15
2022-02-16 20:00 | 44608.8333 | 11256.76
2022-02-16 21:00 | 44608.875 | 11362.64
2022-02-16 22:00 | 44608.9167 | 11182.1
2022-02-16 23:00 | 44608.9583 | 10550.95
2022-02-17 | 44609 | 9618.571
2022-02-17 01:00 | 44609.0417 | 9269.416
2022-02-17 02:00 | 44609.0833 | 9048.878
2022-02-17 03:00 | 44609.125 | 8979.022
2022-02-17 04:00 | 44609.1667 | 8966.48
2022-02-17 05:00 | 44609.2083 | 9234.231
2022-02-17 06:00 | 44609.25 | 9594.679
2022-02-17 07:00 | 44609.2917 | 9983.512
2022-02-17 08:00 | 44609.3333 | 10354.46
2022-02-17 09:00 | 44609.375 | 10573.03
2022-02-17 10:00 | 44609.4167 | 10769.85
2022-02-17 11:00 | 44609.4583 | 10637.14
2022-02-17 12:00 | 44609.5 | 10473.42
2022-02-17 13:00 | 44609.5417 | 10320.7
2022-02-17 14:00 | 44609.5833 | 10283.75
2022-02-17 15:00 | 44609.625 | 10345.23
2022-02-17 16:00 | 44609.6667 | 10803.42
2022-02-17 17:00 | 44609.7083 | 11077.67
2022-02-17 18:00 | 44609.75 | 11054.2
2022-02-17 19:00 | 44609.7917 | 10808.34
2022-02-17 20:00 | 44609.8333 | 10507.74
2022-02-17 21:00 | 44609.875 | 10620.58
2022-02-17 22:00 | 44609.9167 | 10512.16
2022-02-17 23:00 | 44609.9583 | 10008.96
2022-02-18 | 44610 | 9337.702
2022-02-18 01:00 | 44610.0417 | 8899.736
2022-02-18 02:00 | 44610.0833 | 8609.793
2022-02-18 03:00 | 44610.125 | 8432.858
2022-02-18 04:00 | 44610.1667 | 8296.692
2022-02-18 05:00 | 44610.2083 | 8387.139
2022-02-18 06:00 | 44610.25 | 8721.416
2022-02-18 07:00 | 44610.2917 | 9260.344
2022-02-18 08:00 | 44610.3333 | 9800.259
2022-02-18 09:00 | 44610.375 | 10128.14
2022-02-18 10:00 | 44610.4167 | 10429.32
2022-02-18 11:00 | 44610.4583 | 10259.62
2022-02-18 12:00 | 44610.5 | 9994.885
2022-02-18 13:00 | 44610.5417 | 9776.473
2022-02-18 14:00 | 44610.5833 | 9719.989
2022-02-18 15:00 | 44610.625 | 9809.805
2022-02-18 16:00 | 44610.6667 | 10391.85
2022-02-18 17:00 | 44610.7083 | 10841.81
2022-02-18 18:00 | 44610.75 | 10876.8
2022-02-18 19:00 | 44610.7917 | 10704.38
2022-02-18 20:00 | 44610.8333 | 10380.07
2022-02-18 21:00 | 44610.875 | 10498.87
2022-02-18 22:00 | 44610.9167 | 10347.94
2022-02-18 23:00 | 44610.9583 | 9745.902
2022-02-19 | 44611 | 9922.606
2022-02-19 01:00 | 44611.0417 | 9558.877
2022-02-19 02:00 | 44611.0833 | 9410.44
2022-02-19 03:00 | 44611.125 | 9424.958
2022-02-19 04:00 | 44611.1667 | 9854.666
2022-02-19 05:00 | 44611.2083 | 10747.53
2022-02-19 06:00 | 44611.25 | 11409.79
2022-02-19 07:00 | 44611.2917 | 11733.79
2022-02-19 08:00 | 44611.3333 | 11970.38
2022-02-19 09:00 | 44611.375 | 12094.91
2022-02-19 10:00 | 44611.4167 | 12168.66
2022-02-19 11:00 | 44611.4583 | 12026.2
2022-02-19 12:00 | 44611.5 | 11974.64
2022-02-19 13:00 | 44611.5417 | 11862.01
2022-02-19 14:00 | 44611.5833 | 11833.67
2022-02-19 15:00 | 44611.625 | 11877.84
2022-02-19 16:00 | 44611.6667 | 12346.79
2022-02-19 17:00 | 44611.7083 | 12464.19
2022-02-19 18:00 | 44611.75 | 12156.6
2022-02-19 19:00 | 44611.7917 | 11631.34
2022-02-19 20:00 | 44611.8333 | 11205.26
2022-02-19 21:00 | 44611.875 | 11337.02
2022-02-19 22:00 | 44611.9167 | 11184.02
2022-02-19 23:00 | 44611.9583 | 10538.64
2022-02-20 | 44612 | 9876.574
2022-02-20 01:00 | 44612.0417 | 9511.687
2022-02-20 02:00 | 44612.0833 | 9364.783
2022-02-20 03:00 | 44612.125 | 9387.89
2022-02-20 04:00 | 44612.1667 | 9822.869
2022-02-20 05:00 | 44612.2083 | 10717.72
2022-02-20 06:00 | 44612.25 | 11383.22
2022-02-20 07:00 | 44612.2917 | 11717.43
2022-02-20 08:00 | 44612.3333 | 11960.41
2022-02-20 09:00 | 44612.375 | 12091.36
2022-02-20 10:00 | 44612.4167 | 12161.37
2022-02-20 11:00 | 44612.4583 | 12015.18
2022-02-20 12:00 | 44612.5 | 11957.31
2022-02-20 13:00 | 44612.5417 | 11841.89
2022-02-20 14:00 | 44612.5833 | 11811.25
2022-02-20 15:00 | 44612.625 | 11857.29
2022-02-20 16:00 | 44612.6667 | 12322.1
2022-02-20 17:00 | 44612.7083 | 12439.21
2022-02-20 18:00 | 44612.75 | 12137.87
2022-02-20 19:00 | 44612.7917 | 11617.52
2022-02-20 20:00 | 44612.8333 | 11200.89
2022-02-20 21:00 | 44612.875 | 11321.25
2022-02-20 22:00 | 44612.9167 | 11149
2022-02-20 23:00 | 44612.9583 | 10495.69
2022-02-21 | 44613 | 9874.333
2022-02-21 01:00 | 44613.0417 | 9514.417
2022-02-21 02:00 | 44613.0833 | 9370.103
2022-02-21 03:00 | 44613.125 | 9391.095
2022-02-21 04:00 | 44613.1667 | 9817.144
2022-02-21 05:00 | 44613.2083 | 10692.39
2022-02-21 06:00 | 44613.25 | 11345.19
2022-02-21 07:00 | 44613.2917 | 11677.26
2022-02-21 08:00 | 44613.3333 | 11919.37
2022-02-21 09:00 | 44613.375 | 12050.65
2022-02-21 10:00 | 44613.4167 | 12119.8
2022-02-21 11:00 | 44613.4583 | 11974.88
2022-02-21 12:00 | 44613.5 | 11915.22
2022-02-21 13:00 | 44613.5417 | 11801.18
2022-02-21 14:00 | 44613.5833 | 11770.45
2022-02-21 15:00 | 44613.625 | 11816.25
2022-02-21 16:00 | 44613.6667 | 12272.8
2022-02-21 17:00 | 44613.7083 | 12389.2
2022-02-21 18:00 | 44613.75 | 12097.52
2022-02-21 19:00 | 44613.7917 | 11589.21
2022-02-21 20:00 | 44613.8333 | 11182.41
2022-02-21 21:00 | 44613.875 | 11298.49
2022-02-21 22:00 | 44613.9167 | 11125.5
2022-02-21 23:00 | 44613.9583 | 10482.18
2022-02-22 | 44614 | 9857.719
2022-02-22 01:00 | 44614.0417 | 9497.996
2022-02-22 02:00 | 44614.0833 | 9353.948
2022-02-22 03:00 | 44614.125 | 9372.26
2022-02-22 04:00 | 44614.1667 | 9797.026
2022-02-22 05:00 | 44614.2083 | 10662.17
2022-02-22 06:00 | 44614.25 | 11310.63
2022-02-22 07:00 | 44614.2917 | 11647.71
2022-02-22 08:00 | 44614.3333 | 11894.41
2022-02-22 09:00 | 44614.375 | 12029.81
2022-02-22 10:00 | 44614.4167 | 12099.54
2022-02-22 11:00 | 44614.4583 | 11953.3
2022-02-22 12:00 | 44614.5 | 11889.08
2022-02-22 13:00 | 44614.5417 | 11772.72
2022-02-22 14:00 | 44614.5833 | 11741.01
2022-02-22 15:00 | 44614.625 | 11787.92
2022-02-22 16:00 | 44614.6667 | 12241.9
2022-02-22 17:00 | 44614.7083 | 12360.54
2022-02-22 18:00 | 44614.75 | 12076.65
2022-02-22 19:00 | 44614.7917 | 11575.5
2022-02-22 20:00 | 44614.8333 | 11175.34
2022-02-22 21:00 | 44614.875 | 11285.96
2022-02-22 22:00 | 44614.9167 | 11105.52
2022-02-22 23:00 | 44614.9583 | 10461.87
2022-02-23 | 44615 | 9823.44
2022-02-23 01:00 | 44615.0417 | 9464.129
2022-02-23 02:00 | 44615.0833 | 9321.584
2022-02-23 03:00 | 44615.125 | 9348.512
2022-02-23 04:00 | 44615.1667 | 9776.852
2022-02-23 05:00 | 44615.2083 | 10650.44
2022-02-23 06:00 | 44615.25 | 11303.07
2022-02-23 07:00 | 44615.2917 | 11640.92
2022-02-23 08:00 | 44615.3333 | 11886.43
2022-02-23 09:00 | 44615.375 | 12021.62
2022-02-23 10:00 | 44615.4167 | 12088.24
2022-02-23 11:00 | 44615.4583 | 11941.25
2022-02-23 12:00 | 44615.5 | 11877.39
2022-02-23 13:00 | 44615.5417 | 11760.76
2022-02-23 14:00 | 44615.5833 | 11728.73
2022-02-23 15:00 | 44615.625 | 11775.77
2022-02-23 16:00 | 44615.6667 | 12227.89
2022-02-23 17:00 | 44615.7083 | 12343.27
2022-02-23 18:00 | 44615.75 | 12057.06
2022-02-23 19:00 | 44615.7917 | 11554.04
2022-02-23 20:00 | 44615.8333 | 11155.49
2022-02-23 21:00 | 44615.875 | 11263.02
2022-02-23 22:00 | 44615.9167 | 11077.12
2022-02-23 23:00 | 44615.9583 | 10430.78
2022-02-24 | 44616 | 9440.788
2022-02-24 01:00 | 44616.0417 | 9091.79
2022-02-24 02:00 | 44616.0833 | 8873.259
2022-02-24 03:00 | 44616.125 | 8799.994
2022-02-24 04:00 | 44616.1667 | 8787.888
2022-02-24 05:00 | 44616.2083 | 9042.054
2022-02-24 06:00 | 44616.25 | 9397.436
2022-02-24 07:00 | 44616.2917 | 9791.909
2022-02-24 08:00 | 44616.3333 | 10168.25
2022-02-24 09:00 | 44616.375 | 10391.42
2022-02-24 10:00 | 44616.4167 | 10588.1
2022-02-24 11:00 | 44616.4583 | 10453.84
2022-02-24 12:00 | 44616.5 | 10285.11
2022-02-24 13:00 | 44616.5417 | 10130.56
2022-02-24 14:00 | 44616.5833 | 10092.51
2022-02-24 15:00 | 44616.625 | 10155.27
2022-02-24 16:00 | 44616.6667 | 10610.72
2022-02-24 17:00 | 44616.7083 | 10888.08
2022-02-24 18:00 | 44616.75 | 10868.16
2022-02-24 19:00 | 44616.7917 | 10634.28
2022-02-24 20:00 | 44616.8333 | 10341.08
2022-02-24 21:00 | 44616.875 | 10447.82
2022-02-24 22:00 | 44616.9167 | 10331.04
2022-02-24 23:00 | 44616.9583 | 9827.468
2022-02-25 | 44617 | 9152.669
2022-02-25 01:00 | 44617.0417 | 8710.947
2022-02-25 02:00 | 44617.0833 | 8419.896
2022-02-25 03:00 | 44617.125 | 8241.374
2022-02-25 04:00 | 44617.1667 | 8111.729
2022-02-25 05:00 | 44617.2083 | 8196.585
2022-02-25 06:00 | 44617.25 | 8538.102
2022-02-25 07:00 | 44617.2917 | 9087.121
2022-02-25 08:00 | 44617.3333 | 9635.51
2022-02-25 09:00 | 44617.375 | 9969.961
2022-02-25 10:00 | 44617.4167 | 10271.5
2022-02-25 11:00 | 44617.4583 | 10098.41
2022-02-25 12:00 | 44617.5 | 9827.692
2022-02-25 13:00 | 44617.5417 | 9605.008
2022-02-25 14:00 | 44617.5833 | 9546.938
2022-02-25 15:00 | 44617.625 | 9638.848
2022-02-25 16:00 | 44617.6667 | 10223.64
2022-02-25 17:00 | 44617.7083 | 10678.73
2022-02-25 18:00 | 44617.75 | 10718.44
2022-02-25 19:00 | 44617.7917 | 10546.37
2022-02-25 20:00 | 44617.8333 | 10225.36
2022-02-25 21:00 | 44617.875 | 10338.29
2022-02-25 22:00 | 44617.9167 | 10175.19
2022-02-25 23:00 | 44617.9583 | 9564.526
2022-02-26 | 44618 | 9702.249
2022-02-26 01:00 | 44618.0417 | 9341.639
2022-02-26 02:00 | 44618.0833 | 9199.741
2022-02-26 03:00 | 44618.125 | 9226.021
2022-02-26 04:00 | 44618.1667 | 9663.365
2022-02-26 05:00 | 44618.2083 | 10540.48
2022-02-26 06:00 | 44618.25 | 11196.3
2022-02-26 07:00 | 44618.2917 | 11539.39
2022-02-26 08:00 | 44618.3333 | 11788.03
2022-02-26 09:00 | 44618.375 | 11926.15
2022-02-26 10:00 | 44618.4167 | 11990.7
2022-02-26 11:00 | 44618.4583 | 11841.55
2022-02-26 12:00 | 44618.5 | 11774.72
2022-02-26 13:00 | 44618.5417 | 11657.72
2022-02-26 14:00 | 44618.5833 | 11624.49
2022-02-26 15:00 | 44618.625 | 11672.38
2022-02-26 16:00 | 44618.6667 | 12123.32
2022-02-26 17:00 | 44618.7083 | 12238.45
2022-02-26 18:00 | 44618.75 | 11953.87
2022-02-26 19:00 | 44618.7917 | 11451.71
2022-02-26 20:00 | 44618.8333 | 11056.61
2022-02-26 21:00 | 44618.875 | 11159.05
2022-02-26 22:00 | 44618.9167 | 10963.76
2022-02-26 23:00 | 44618.9583 | 10312.34
2022-02-27 | 44619 | 9683.199
2022-02-27 01:00 | 44619.0417 | 9319.716
2022-02-27 02:00 | 44619.0833 | 9175.088
2022-02-27 03:00 | 44619.125 | 9202.14
2022-02-27 04:00 | 44619.1667 | 9642.466
2022-02-27 05:00 | 44619.2083 | 10539.47
2022-02-27 06:00 | 44619.25 | 11205.51
2022-02-27 07:00 | 44619.2917 | 11541.25
2022-02-27 08:00 | 44619.3333 | 11784.08
2022-02-27 09:00 | 44619.375 | 11915.84
2022-02-27 10:00 | 44619.4167 | 11981.91
2022-02-27 11:00 | 44619.4583 | 11834.64
2022-02-27 12:00 | 44619.5 | 11775.53
2022-02-27 13:00 | 44619.5417 | 11660.4
2022-02-27 14:00 | 44619.5833 | 11629.22
2022-02-27 15:00 | 44619.625 | 11675.63
2022-02-27 16:00 | 44619.6667 | 12136.18
2022-02-27 17:00 | 44619.7083 | 12250.2
2022-02-27 18:00 | 44619.75 | 11950
2022-02-27 19:00 | 44619.7917 | 11431.87
2022-02-27 20:00 | 44619.8333 | 11020.52
2022-02-27 21:00 | 44619.875 | 11135.52
2022-02-27 22:00 | 44619.9167 | 10955.76
2022-02-27 23:00 | 44619.9583 | 10301.71
2022-02-28 | 44620 | 9669.017
2022-02-28 01:00 | 44620.0417 | 9301.831
2022-02-28 02:00 | 44620.0833 | 9155.041
2022-02-28 03:00 | 44620.125 | 9180.109
2022-02-28 04:00 | 44620.1667 | 9628.85
2022-02-28 05:00 | 44620.2083 | 10540.77
2022-02-28 06:00 | 44620.25 | 11216.11
2022-02-28 07:00 | 44620.2917 | 11551.83
2022-02-28 08:00 | 44620.3333 | 11794.42
2022-02-28 09:00 | 44620.375 | 11924.95
2022-02-28 10:00 | 44620.4167 | 11991.49
2022-02-28 11:00 | 44620.4583 | 11843.76
2022-02-28 12:00 | 44620.5 | 11787.08
2022-02-28 13:00 | 44620.5417 | 11671.82
2022-02-28 14:00 | 44620.5833 | 11641.07
2022-02-28 15:00 | 44620.625 | 11687.37
2022-02-28 16:00 | 44620.6667 | 12155.08
2022-02-28 17:00 | 44620.7083 | 12269.54
2022-02-28 18:00 | 44620.75 | 11960.75
2022-02-28 19:00 | 44620.7917 | 11432.53
2022-02-28 20:00 | 44620.8333 | 11012.1
2022-02-28 21:00 | 44620.875 | 11132.27
2022-02-28 22:00 | 44620.9167 | 10956.26
2022-02-28 23:00 | 44620.9583 | 10295.9
2022-03-01 | 44621 | 9650.773
2022-03-01 01:00 | 44621.0417 | 9283.999
2022-03-01 02:00 | 44621.0833 | 9137.322
2022-03-01 03:00 | 44621.125 | 9162.234
2022-03-01 04:00 | 44621.1667 | 9603.87
2022-03-01 05:00 | 44621.2083 | 10504.01
2022-03-01 06:00 | 44621.25 | 11173.83
2022-03-01 07:00 | 44621.2917 | 11513.23
2022-03-01 08:00 | 44621.3333 | 11759.71
2022-03-01 09:00 | 44621.375 | 11893.55
2022-03-01 10:00 | 44621.4167 | 11961.68
2022-03-01 11:00 | 44621.4583 | 11813.24
2022-03-01 12:00 | 44621.5 | 11752.68
2022-03-01 13:00 | 44621.5417 | 11635.27
2022-03-01 14:00 | 44621.5833 | 11603.7
2022-03-01 15:00 | 44621.625 | 11650.85
2022-03-01 16:00 | 44621.6667 | 12116.97
2022-03-01 17:00 | 44621.7083 | 12233.96
2022-03-01 18:00 | 44621.75 | 11932.65
2022-03-01 19:00 | 44621.7917 | 11411.58
2022-03-01 20:00 | 44621.8333 | 10996.78
2022-03-01 21:00 | 44621.875 | 11113.05
2022-03-01 22:00 | 44621.9167 | 10932.41
2022-03-01 23:00 | 44621.9583 | 10273.2
2022-03-02 | 44622 | 9703.752
2022-03-02 01:00 | 44622.0417 | 9348.538
2022-03-02 02:00 | 44622.0833 | 9209.078
2022-03-02 03:00 | 44622.125 | 9232.418
2022-03-02 04:00 | 44622.1667 | 9659.971
2022-03-02 05:00 | 44622.2083 | 10516.66
2022-03-02 06:00 | 44622.25 | 11159.07
2022-03-02 07:00 | 44622.2917 | 11499.12
2022-03-02 08:00 | 44622.3333 | 11746.62
2022-03-02 09:00 | 44622.375 | 11884.74
2022-03-02 10:00 | 44622.4167 | 11948.46
2022-03-02 11:00 | 44622.4583 | 11801.11
2022-03-02 12:00 | 44622.5 | 11733.19
2022-03-02 13:00 | 44622.5417 | 11616.61
2022-03-02 14:00 | 44622.5833 | 11583.69
2022-03-02 15:00 | 44622.625 | 11631.38
2022-03-02 16:00 | 44622.6667 | 12074.73
2022-03-02 17:00 | 44622.7083 | 12189.38
2022-03-02 18:00 | 44622.75 | 11914.21
2022-03-02 19:00 | 44622.7917 | 11423.92
2022-03-02 20:00 | 44622.8333 | 11037.94
2022-03-02 21:00 | 44622.875 | 11137.11
2022-03-02 22:00 | 44622.9167 | 10942.96
2022-03-02 23:00 | 44622.9583 | 10302.56
2022-03-03 | 44623 | 9429.016
2022-03-03 01:00 | 44623.0417 | 9081.921
2022-03-03 02:00 | 44623.0833 | 8871.982
2022-03-03 03:00 | 44623.125 | 8802.068
2022-03-03 04:00 | 44623.1667 | 8797.133
2022-03-03 05:00 | 44623.2083 | 9043.036
2022-03-03 06:00 | 44623.25 | 9396.794
2022-03-03 07:00 | 44623.2917 | 9800.779
2022-03-03 08:00 | 44623.3333 | 10182.52
2022-03-03 09:00 | 44623.375 | 10412.13
2022-03-03 10:00 | 44623.4167 | 10603.17
2022-03-03 11:00 | 44623.4583 | 10465.41
2022-03-03 12:00 | 44623.5 | 10289.32
2022-03-03 13:00 | 44623.5417 | 10132.04
2022-03-03 14:00 | 44623.5833 | 10091.59
2022-03-03 15:00 | 44623.625 | 10156.34
2022-03-03 16:00 | 44623.6667 | 10602.62
2022-03-03 17:00 | 44623.7083 | 10878.19
2022-03-03 18:00 | 44623.75 | 10862.52
2022-03-03 19:00 | 44623.7917 | 10645.61
2022-03-03 20:00 | 44623.8333 | 10368.39
2022-03-03 21:00 | 44623.875 | 10459.71
2022-03-03 22:00 | 44623.9167 | 10320.56
2022-03-03 23:00 | 44623.9583 | 9813.542
2022-03-04 | 44624 | 9137.462
2022-03-04 01:00 | 44624.0417 | 8696.806
2022-03-04 02:00 | 44624.0833 | 8406.911
2022-03-04 03:00 | 44624.125 | 8231.999
2022-03-04 04:00 | 44624.1667 | 8105.118
2022-03-04 05:00 | 44624.2083 | 8191.736
2022-03-04 06:00 | 44624.25 | 8532.058
2022-03-04 07:00 | 44624.2917 | 9083.367
2022-03-04 08:00 | 44624.3333 | 9632.599
2022-03-04 09:00 | 44624.375 | 9968.465
2022-03-04 10:00 | 44624.4167 | 10266.54
2022-03-04 11:00 | 44624.4583 | 10092.35
2022-03-04 12:00 | 44624.5 | 9819.962
2022-03-04 13:00 | 44624.5417 | 9596.764
2022-03-04 14:00 | 44624.5833 | 9538.165
2022-03-04 15:00 | 44624.625 | 9630.611
2022-03-04 16:00 | 44624.6667 | 10212.34
2022-03-04 17:00 | 44624.7083 | 10664.65
2022-03-04 18:00 | 44624.75 | 10709.35
2022-03-04 19:00 | 44624.7917 | 10538.2
2022-03-04 20:00 | 44624.8333 | 10222.36
2022-03-04 21:00 | 44624.875 | 10330.25
2022-03-04 22:00 | 44624.9167 | 10160
2022-03-04 23:00 | 44624.9583 | 9548.512
2022-03-05 | 44625 | 9685.892
2022-03-05 01:00 | 44625.0417 | 9329.734
2022-03-05 02:00 | 44625.0833 | 9190.161
2022-03-05 03:00 | 44625.125 | 9215.59
2022-03-05 04:00 | 44625.1667 | 9646.652
2022-03-05 05:00 | 44625.2083 | 10505.02
2022-03-05 06:00 | 44625.25 | 11149.71
2022-03-05 07:00 | 44625.2917 | 11494.85
2022-03-05 08:00 | 44625.3333 | 11745.66
2022-03-05 09:00 | 44625.375 | 11886.71
2022-03-05 10:00 | 44625.4167 | 11949.49
2022-03-05 11:00 | 44625.4583 | 11800.2
2022-03-05 12:00 | 44625.5 | 11729.27
2022-03-05 13:00 | 44625.5417 | 11610.87
2022-03-05 14:00 | 44625.5833 | 11576.94
2022-03-05 15:00 | 44625.625 | 11625.59
2022-03-05 16:00 | 44625.6667 | 12068.63
2022-03-05 17:00 | 44625.7083 | 12183.78
2022-03-05 18:00 | 44625.75 | 11910.77
2022-03-05 19:00 | 44625.7917 | 11421.68
2022-03-05 20:00 | 44625.8333 | 11038.76
2022-03-05 21:00 | 44625.875 | 11133.46
2022-03-05 22:00 | 44625.9167 | 10931.04
2022-03-05 23:00 | 44625.9583 | 10286.02
2022-03-06 | 44626 | 9608.644
2022-03-06 01:00 | 44626.0417 | 9252.998
2022-03-06 02:00 | 44626.0833 | 9115.12
2022-03-06 03:00 | 44626.125 | 9144.118
2022-03-06 04:00 | 44626.1667 | 9580.326
2022-03-06 05:00 | 44626.2083 | 10440.45
2022-03-06 06:00 | 44626.25 | 11086.22
2022-03-06 07:00 | 44626.2917 | 11434.58
2022-03-06 08:00 | 44626.3333 | 11686.62
2022-03-06 09:00 | 44626.375 | 11829.61
2022-03-06 10:00 | 44626.4167 | 11889.34
2022-03-06 11:00 | 44626.4583 | 11738.69
2022-03-06 12:00 | 44626.5 | 11665.69
2022-03-06 13:00 | 44626.5417 | 11546.69
2022-03-06 14:00 | 44626.5833 | 11511.86
2022-03-06 15:00 | 44626.625 | 11561.1
2022-03-06 16:00 | 44626.6667 | 12000.54
2022-03-06 17:00 | 44626.7083 | 12113.8
2022-03-06 18:00 | 44626.75 | 11843.1
2022-03-06 19:00 | 44626.7917 | 11356.5
2022-03-06 20:00 | 44626.8333 | 10978.92
2022-03-06 21:00 | 44626.875 | 11067.86
2022-03-06 22:00 | 44626.9167 | 10856.62
2022-03-06 23:00 | 44626.9583 | 10209.42
2022-03-07 | 44627 | 9549.712
2022-03-07 01:00 | 44627.0417 | 9191.915
2022-03-07 02:00 | 44627.0833 | 9053.563
2022-03-07 03:00 | 44627.125 | 9082.618
2022-03-07 04:00 | 44627.1667 | 9524.352
2022-03-07 05:00 | 44627.2083 | 10392.51
2022-03-07 06:00 | 44627.25 | 11043.41
2022-03-07 07:00 | 44627.2917 | 11392.95
2022-03-07 08:00 | 44627.3333 | 11645.37
2022-03-07 09:00 | 44627.375 | 11788.34
2022-03-07 10:00 | 44627.4167 | 11848.16
2022-03-07 11:00 | 44627.4583 | 11696.79
2022-03-07 12:00 | 44627.5 | 11624.2
2022-03-07 13:00 | 44627.5417 | 11504.46
2022-03-07 14:00 | 44627.5833 | 11469.53
2022-03-07 15:00 | 44627.625 | 11518.94
2022-03-07 16:00 | 44627.6667 | 11961.04
2022-03-07 17:00 | 44627.7083 | 12074.36
2022-03-07 18:00 | 44627.75 | 11800.13
2022-03-07 19:00 | 44627.7917 | 11309.09
2022-03-07 20:00 | 44627.8333 | 10928.34
2022-03-07 21:00 | 44627.875 | 11018.24
2022-03-07 22:00 | 44627.9167 | 10806.2
2022-03-07 23:00 | 44627.9583 | 10154.88
2022-03-08 | 44628 | 9544.105
2022-03-08 01:00 | 44628.0417 | 9196.945
2022-03-08 02:00 | 44628.0833 | 9065.957
2022-03-08 03:00 | 44628.125 | 9097.574
2022-03-08 04:00 | 44628.1667 | 9531.482
2022-03-08 05:00 | 44628.2083 | 10368.28
2022-03-08 06:00 | 44628.25 | 10998.17
2022-03-08 07:00 | 44628.2917 | 11347.55
2022-03-08 08:00 | 44628.3333 | 11598.93
2022-03-08 09:00 | 44628.375 | 11744.57
2022-03-08 10:00 | 44628.4167 | 11798.1
2022-03-08 11:00 | 44628.4583 | 11647.39
2022-03-08 12:00 | 44628.5 | 11569.25
2022-03-08 13:00 | 44628.5417 | 11451.41
2022-03-08 14:00 | 44628.5833 | 11415.19
2022-03-08 15:00 | 44628.625 | 11464.87
2022-03-08 16:00 | 44628.6667 | 11886.09
2022-03-08 17:00 | 44628.7083 | 11994.48
2022-03-08 18:00 | 44628.75 | 11740.25
2022-03-08 19:00 | 44628.7917 | 11273.94
2022-03-08 20:00 | 44628.8333 | 10918.58
2022-03-08 21:00 | 44628.875 | 10992.29
2022-03-08 22:00 | 44628.9167 | 10766.2
2022-03-08 23:00 | 44628.9583 | 10130
2022-03-09 | 44629 | 9523.291
2022-03-09 01:00 | 44629.0417 | 9170.956
2022-03-09 02:00 | 44629.0833 | 9037.55
2022-03-09 03:00 | 44629.125 | 9068.48
2022-03-09 04:00 | 44629.1667 | 9511.165
2022-03-09 05:00 | 44629.2083 | 10358.2
2022-03-09 06:00 | 44629.25 | 10997.18
2022-03-09 07:00 | 44629.2917 | 11354.79
2022-03-09 08:00 | 44629.3333 | 11612.33
2022-03-09 09:00 | 44629.375 | 11762.29
2022-03-09 10:00 | 44629.4167 | 11816.54
2022-03-09 11:00 | 44629.4583 | 11662.77
2022-03-09 12:00 | 44629.5 | 11581.39
2022-03-09 13:00 | 44629.5417 | 11460.8
2022-03-09 14:00 | 44629.5833 | 11423.33
2022-03-09 15:00 | 44629.625 | 11474.36
2022-03-09 16:00 | 44629.6667 | 11901.42
2022-03-09 17:00 | 44629.7083 | 12012.83
2022-03-09 18:00 | 44629.75 | 11756.85
2022-03-09 19:00 | 44629.7917 | 11285.69
2022-03-09 20:00 | 44629.8333 | 10927.47
2022-03-09 21:00 | 44629.875 | 10999.46
2022-03-09 22:00 | 44629.9167 | 10765.39
2022-03-09 23:00 | 44629.9583 | 10117.92
2022-03-10 | 44630 | 9244.705
2022-03-10 01:00 | 44630.0417 | 8901.069
2022-03-10 02:00 | 44630.0833 | 8692.022
2022-03-10 03:00 | 44630.125 | 8621.444
2022-03-10 04:00 | 44630.1667 | 8612.082
2022-03-10 05:00 | 44630.2083 | 8828.868
2022-03-10 06:00 | 44630.25 | 9168.646
2022-03-10 07:00 | 44630.2917 | 9580.879
2022-03-10 08:00 | 44630.3333 | 9969.798
2022-03-10 09:00 | 44630.375 | 10206.77
2022-03-10 10:00 | 44630.4167 | 10396.19
2022-03-10 11:00 | 44630.4583 | 10256.36
2022-03-10 12:00 | 44630.5 | 10071.08
2022-03-10 13:00 | 44630.5417 | 9912.294
2022-03-10 14:00 | 44630.5833 | 9869.691
2022-03-10 15:00 | 44630.625 | 9936.206
2022-03-10 16:00 | 44630.6667 | 10372.23
2022-03-10 17:00 | 44630.7083 | 10657.42
2022-03-10 18:00 | 44630.75 | 10647.44
2022-03-10 19:00 | 44630.7917 | 10455.82
2022-03-10 20:00 | 44630.8333 | 10197.17
2022-03-10 21:00 | 44630.875 | 10274.94
2022-03-10 22:00 | 44630.9167 | 10119.86
2022-03-10 23:00 | 44630.9583 | 9617.314
2022-03-11 | 44631 | 8942.374
2022-03-11 01:00 | 44631.0417 | 8506.722
2022-03-11 02:00 | 44631.0833 | 8226.357
2022-03-11 03:00 | 44631.125 | 8066.338
2022-03-11 04:00 | 44631.1667 | 7947.621
2022-03-11 05:00 | 44631.2083 | 8013.049
2022-03-11 06:00 | 44631.25 | 8341.871
2022-03-11 07:00 | 44631.2917 | 8920.275
2022-03-11 08:00 | 44631.3333 | 9486.31
2022-03-11 09:00 | 44631.375 | 9841.535
2022-03-11 10:00 | 44631.4167 | 10127.19
2022-03-11 11:00 | 44631.4583 | 9943.773
2022-03-11 12:00 | 44631.5 | 9649.445
2022-03-11 13:00 | 44631.5417 | 9419.287
2022-03-11 14:00 | 44631.5833 | 9353.571
2022-03-11 15:00 | 44631.625 | 9451.267
2022-03-11 16:00 | 44631.6667 | 10006.32
2022-03-11 17:00 | 44631.7083 | 10461
2022-03-11 18:00 | 44631.75 | 10530.31
2022-03-11 19:00 | 44631.7917 | 10398.04
2022-03-11 20:00 | 44631.8333 | 10127.22
2022-03-11 21:00 | 44631.875 | 10193.01
2022-03-11 22:00 | 44631.9167 | 9962.635
2022-03-11 23:00 | 44631.9583 | 9343.655
2022-03-12 | 44632 | 9564.972
2022-03-12 01:00 | 44632.0417 | 9219.272
2022-03-12 02:00 | 44632.0833 | 9089.057
2022-03-12 03:00 | 44632.125 | 9118.941
2022-03-12 04:00 | 44632.1667 | 9550.953
2022-03-12 05:00 | 44632.2083 | 10378.31
2022-03-12 06:00 | 44632.25 | 11003.24
2022-03-12 07:00 | 44632.2917 | 11355.29
2022-03-12 08:00 | 44632.3333 | 11609.07
2022-03-12 09:00 | 44632.375 | 11757.18
2022-03-12 10:00 | 44632.4167 | 11809.94
2022-03-12 11:00 | 44632.4583 | 11658.64
2022-03-12 12:00 | 44632.5 | 11577.55
2022-03-12 13:00 | 44632.5417 | 11458.87
2022-03-12 14:00 | 44632.5833 | 11422.08
2022-03-12 15:00 | 44632.625 | 11472.39
2022-03-12 16:00 | 44632.6667 | 11890.34
2022-03-12 17:00 | 44632.7083 | 11999.5
2022-03-12 18:00 | 44632.75 | 11751.65
2022-03-12 19:00 | 44632.7917 | 11291.96
2022-03-12 20:00 | 44632.8333 | 10942.82
2022-03-12 21:00 | 44632.875 | 11012.2
2022-03-12 22:00 | 44632.9167 | 10781.24
2022-03-12 23:00 | 44632.9583 | 10146.96
2022-03-13 | 44633 | 9562.641
2022-03-13 01:00 | 44633.0417 | 9214.594
2022-03-13 02:00 | 44633.0833 | 9082.873
2022-03-13 03:00 | 44633.125 | 9113.49
2022-03-13 04:00 | 44633.1667 | 9541.442
2022-03-13 05:00 | 44633.2083 | 10365.04
2022-03-13 06:00 | 44633.25 | 10990.26
2022-03-13 07:00 | 44633.2917 | 11348.19
2022-03-13 08:00 | 44633.3333 | 11607.45
2022-03-13 09:00 | 44633.375 | 11759.56
2022-03-13 10:00 | 44633.4167 | 11814.46
2022-03-13 11:00 | 44633.4583 | 11661.46
2022-03-13 12:00 | 44633.5 | 11576.55
2022-03-13 13:00 | 44633.5417 | 11455
2022-03-13 14:00 | 44633.5833 | 11417.28
2022-03-13 15:00 | 44633.625 | 11468.74
2022-03-13 16:00 | 44633.6667 | 11888.86
2022-03-13 17:00 | 44633.7083 | 12001.89
2022-03-13 18:00 | 44633.75 | 11758.1
2022-03-13 19:00 | 44633.7917 | 11300.49
2022-03-13 20:00 | 44633.8333 | 10952.64
2022-03-13 21:00 | 44633.875 | 11019.79
2022-03-13 22:00 | 44633.9167 | 10783.71
2022-03-13 23:00 | 44633.9583 | 10145.21
2022-03-14 | 44634 | 9542.272
2022-03-14 01:00 | 44634.0417 | 9193.312
2022-03-14 02:00 | 44634.0833 | 9061.178
2022-03-14 03:00 | 44634.125 | 9089.908
2022-03-14 04:00 | 44634.1667 | 9517.649
2022-03-14 05:00 | 44634.2083 | 10341.62
2022-03-14 06:00 | 44634.25 | 10967.24
2022-03-14 07:00 | 44634.2917 | 11324.79
2022-03-14 08:00 | 44634.3333 | 11584.14
2022-03-14 09:00 | 44634.375 | 11735.97
2022-03-14 10:00 | 44634.4167 | 11791.48
2022-03-14 11:00 | 44634.4583 | 11638.68
2022-03-14 12:00 | 44634.5 | 11554.26
2022-03-14 13:00 | 44634.5417 | 11433.02
2022-03-14 14:00 | 44634.5833 | 11395.52
2022-03-14 15:00 | 44634.625 | 11446.88
2022-03-14 16:00 | 44634.6667 | 11868.61
2022-03-14 17:00 | 44634.7083 | 11982.43
2022-03-14 18:00 | 44634.75 | 11737.65
2022-03-14 19:00 | 44634.7917 | 11278.79
2022-03-14 20:00 | 44634.8333 | 10928.95
2022-03-14 21:00 | 44634.875 | 10997.91
2022-03-14 22:00 | 44634.9167 | 10764.19
2022-03-14 23:00 | 44634.9583 | 10125.59
2022-03-15 | 44635 | 9437.483
2022-03-15 01:00 | 44635.0417 | 9088.835
2022-03-15 02:00 | 44635.0833 | 8958.14
2022-03-15 03:00 | 44635.125 | 8989.678
2022-03-15 04:00 | 44635.1667 | 9428.806
2022-03-15 05:00 | 44635.2083 | 10263.27
2022-03-15 06:00 | 44635.25 | 10894.11
2022-03-15 07:00 | 44635.2917 | 11252.32
2022-03-15 08:00 | 44635.3333 | 11509.96
2022-03-15 09:00 | 44635.375 | 11661.21
2022-03-15 10:00 | 44635.4167 | 11713.47
2022-03-15 11:00 | 44635.4583 | 11559.79
2022-03-15 12:00 | 44635.5 | 11475.98
2022-03-15 13:00 | 44635.5417 | 11354.83
2022-03-15 14:00 | 44635.5833 | 11316.94
2022-03-15 15:00 | 44635.625 | 11368.3
2022-03-15 16:00 | 44635.6667 | 11788.08
2022-03-15 17:00 | 44635.7083 | 11898.18
2022-03-15 18:00 | 44635.75 | 11650.13
2022-03-15 19:00 | 44635.7917 | 11188.36
2022-03-15 20:00 | 44635.8333 | 10839.7
2022-03-15 21:00 | 44635.875 | 10905.55
2022-03-15 22:00 | 44635.9167 | 10666.03
2022-03-15 23:00 | 44635.9583 | 10024.07
2022-03-16 | 44636 | 9418.308
2022-03-16 01:00 | 44636.0417 | 9073.672
2022-03-16 02:00 | 44636.0833 | 8947.018
2022-03-16 03:00 | 44636.125 | 8983.481
2022-03-16 04:00 | 44636.1667 | 9421.722
2022-03-16 05:00 | 44636.2083 | 10244.19
2022-03-16 06:00 | 44636.25 | 10867.62
2022-03-16 07:00 | 44636.2917 | 11229.77
2022-03-16 08:00 | 44636.3333 | 11489.33
2022-03-16 09:00 | 44636.375 | 11644.23
2022-03-16 10:00 | 44636.4167 | 11692.35
2022-03-16 11:00 | 44636.4583 | 11537.55
2022-03-16 12:00 | 44636.5 | 11449.04
2022-03-16 13:00 | 44636.5417 | 11327.1
2022-03-16 14:00 | 44636.5833 | 11287.79
2022-03-16 15:00 | 44636.625 | 11340.03
2022-03-16 16:00 | 44636.6667 | 11749.01
2022-03-16 17:00 | 44636.7083 | 11856.77
2022-03-16 18:00 | 44636.75 | 11619.58
2022-03-16 19:00 | 44636.7917 | 11170.12
2022-03-16 20:00 | 44636.8333 | 10836.03
2022-03-16 21:00 | 44636.875 | 10890.37
2022-03-16 22:00 | 44636.9167 | 10637.08
2022-03-16 23:00 | 44636.9583 | 9998.351
2022-03-17 | 44637 | 9085.573
2022-03-17 01:00 | 44637.0417 | 8738.704
2022-03-17 02:00 | 44637.0833 | 8533.816
2022-03-17 03:00 | 44637.125 | 8461.48
2022-03-17 04:00 | 44637.1667 | 8459.847
2022-03-17 05:00 | 44637.2083 | 8681.665
2022-03-17 06:00 | 44637.25 | 9025.717
2022-03-17 07:00 | 44637.2917 | 9451.792
2022-03-17 08:00 | 44637.3333 | 9850.119
2022-03-17 09:00 | 44637.375 | 10095.56
2022-03-17 10:00 | 44637.4167 | 10282.93
2022-03-17 11:00 | 44637.4583 | 10138.28
2022-03-17 12:00 | 44637.5 | 9944.528
2022-03-17 13:00 | 44637.5417 | 9780.86
2022-03-17 14:00 | 44637.5833 | 9735.573
2022-03-17 15:00 | 44637.625 | 9804.676
2022-03-17 16:00 | 44637.6667 | 10239.5
2022-03-17 17:00 | 44637.7083 | 10528.09
2022-03-17 18:00 | 44637.75 | 10524.18
2022-03-17 19:00 | 44637.7917 | 10337.08
2022-03-17 20:00 | 44637.8333 | 10087.21
2022-03-17 21:00 | 44637.875 | 10153.09
2022-03-17 22:00 | 44637.9167 | 9976.468
2022-03-17 23:00 | 44637.9583 | 9462.7
2022-03-18 | 44638 | 8844.932
2022-03-18 01:00 | 44638.0417 | 8407.507
2022-03-18 02:00 | 44638.0833 | 8122.99
2022-03-18 03:00 | 44638.125 | 7948.101
2022-03-18 04:00 | 44638.1667 | 7815.398
2022-03-18 05:00 | 44638.2083 | 7868.631
2022-03-18 06:00 | 44638.25 | 8184.147
2022-03-18 07:00 | 44638.2917 | 8761.43
2022-03-18 08:00 | 44638.3333 | 9330.651
2022-03-18 09:00 | 44638.375 | 9686.351
2022-03-18 10:00 | 44638.4167 | 9979.941
2022-03-18 11:00 | 44638.4583 | 9798.22
2022-03-18 12:00 | 44638.5 | 9503.238
2022-03-18 13:00 | 44638.5417 | 9272.146
2022-03-18 14:00 | 44638.5833 | 9207.517
2022-03-18 15:00 | 44638.625 | 9305.258
2022-03-18 16:00 | 44638.6667 | 9867.712
2022-03-18 17:00 | 44638.7083 | 10330.97
2022-03-18 18:00 | 44638.75 | 10404.39
2022-03-18 19:00 | 44638.7917 | 10273.77
2022-03-18 20:00 | 44638.8333 | 9997.327
2022-03-18 21:00 | 44638.875 | 10071.48
2022-03-18 22:00 | 44638.9167 | 9854.799
2022-03-18 23:00 | 44638.9583 | 9240.9
2022-03-19 | 44639 | 9463.561
2022-03-19 01:00 | 44639.0417 | 9115.078
2022-03-19 02:00 | 44639.0833 | 8984.222
2022-03-19 03:00 | 44639.125 | 9014.255
2022-03-19 04:00 | 44639.1667 | 9446.696
2022-03-19 05:00 | 44639.2083 | 10270.33
2022-03-19 06:00 | 44639.25 | 10896.08
2022-03-19 07:00 | 44639.2917 | 11257.09
2022-03-19 08:00 | 44639.3333 | 11517.87
2022-03-19 09:00 | 44639.375 | 11671.65
2022-03-19 10:00 | 44639.4167 | 11725.48
2022-03-19 11:00 | 44639.4583 | 11571.41
2022-03-19 12:00 | 44639.5 | 11484.64
2022-03-19 13:00 | 44639.5417 | 11363.11
2022-03-19 14:00 | 44639.5833 | 11324.73
2022-03-19 15:00 | 44639.625 | 11376.7
2022-03-19 16:00 | 44639.6667 | 11795.26
2022-03-19 17:00 | 44639.7083 | 11908.02
2022-03-19 18:00 | 44639.75 | 11666.25
2022-03-19 19:00 | 44639.7917 | 11210.4
2022-03-19 20:00 | 44639.8333 | 10865.75
2022-03-19 21:00 | 44639.875 | 10929.42
2022-03-19 22:00 | 44639.9167 | 10687.72
2022-03-19 23:00 | 44639.9583 | 10047.34
2022-03-20 | 44640 | 9456.713
2022-03-20 01:00 | 44640.0417 | 9098.85
2022-03-20 02:00 | 44640.0833 | 8959.132
2022-03-20 03:00 | 44640.125 | 8985.172
2022-03-20 04:00 | 44640.1667 | 9417.725
2022-03-20 05:00 | 44640.2083 | 10273.7
2022-03-20 06:00 | 44640.25 | 10919
2022-03-20 07:00 | 44640.2917 | 11271.43
2022-03-20 08:00 | 44640.3333 | 11527.42
2022-03-20 09:00 | 44640.375 | 11672.8
2022-03-20 10:00 | 44640.4167 | 11734.26
2022-03-20 11:00 | 44640.4583 | 11582.59
2022-03-20 12:00 | 44640.5 | 11507.19
2022-03-20 13:00 | 44640.5417 | 11386.54
2022-03-20 14:00 | 44640.5833 | 11351.48
2022-03-20 15:00 | 44640.625 | 11401.6
2022-03-20 16:00 | 44640.6667 | 11845.2
2022-03-20 17:00 | 44640.7083 | 11962.3
2022-03-20 18:00 | 44640.75 | 11693.82
2022-03-20 19:00 | 44640.7917 | 11207.79
2022-03-20 20:00 | 44640.8333 | 10829.2
2022-03-20 21:00 | 44640.875 | 10918.75
2022-03-20 22:00 | 44640.9167 | 10707.17
2022-03-20 23:00 | 44640.9583 | 10057.7
2022-03-21 | 44641 | 9472.492
2022-03-21 01:00 | 44641.0417 | 9125.874
2022-03-21 02:00 | 44641.0833 | 8995.598
2022-03-21 03:00 | 44641.125 | 9026.676
2022-03-21 04:00 | 44641.1667 | 9460.353
2022-03-21 05:00 | 44641.2083 | 10287.32
2022-03-21 06:00 | 44641.25 | 10913.22
2022-03-21 07:00 | 44641.2917 | 11269.88
2022-03-21 08:00 | 44641.3333 | 11526.53
2022-03-21 09:00 | 44641.375 | 11677.2
2022-03-21 10:00 | 44641.4167 | 11729.29
2022-03-21 11:00 | 44641.4583 | 11576.41
2022-03-21 12:00 | 44641.5 | 11492.6
2022-03-21 13:00 | 44641.5417 | 11373.07
2022-03-21 14:00 | 44641.5833 | 11335.44
2022-03-21 15:00 | 44641.625 | 11386.59
2022-03-21 16:00 | 44641.6667 | 11804.42
2022-03-21 17:00 | 44641.7083 | 11914.42
2022-03-21 18:00 | 44641.75 | 11669.1
2022-03-21 19:00 | 44641.7917 | 11211.01
2022-03-21 20:00 | 44641.8333 | 10864.73
2022-03-21 21:00 | 44641.875 | 10930.52
2022-03-21 22:00 | 44641.9167 | 10693.12
2022-03-21 23:00 | 44641.9583 | 10055.61
2022-03-22 | 44642 | 9441.847
2022-03-22 01:00 | 44642.0417 | 9091.755
2022-03-22 02:00 | 44642.0833 | 8957.528
2022-03-22 03:00 | 44642.125 | 8984.664
2022-03-22 04:00 | 44642.1667 | 9405.45
2022-03-22 05:00 | 44642.2083 | 10226.66
2022-03-22 06:00 | 44642.25 | 10851.41
2022-03-22 07:00 | 44642.2917 | 11208.52
2022-03-22 08:00 | 44642.3333 | 11468.48
2022-03-22 09:00 | 44642.375 | 11619.86
2022-03-22 10:00 | 44642.4167 | 11678.02
2022-03-22 11:00 | 44642.4583 | 11525.72
2022-03-22 12:00 | 44642.5 | 11441.78
2022-03-22 13:00 | 44642.5417 | 11320.45
2022-03-22 14:00 | 44642.5833 | 11283.51
2022-03-22 15:00 | 44642.625 | 11334.85
2022-03-22 16:00 | 44642.6667 | 11761.07
2022-03-22 17:00 | 44642.7083 | 11877.46
2022-03-22 18:00 | 44642.75 | 11631.83
2022-03-22 19:00 | 44642.7917 | 11171.39
2022-03-22 20:00 | 44642.8333 | 10817.59
2022-03-22 21:00 | 44642.875 | 10890.72
2022-03-22 22:00 | 44642.9167 | 10662.89
2022-03-22 23:00 | 44642.9583 | 10024.93
2022-03-23 | 44643 | 9403.322
2022-03-23 01:00 | 44643.0417 | 9051.487
2022-03-23 02:00 | 44643.0833 | 8917.69
2022-03-23 03:00 | 44643.125 | 8948.24
2022-03-23 04:00 | 44643.1667 | 9381.984
2022-03-23 05:00 | 44643.2083 | 10216.83
2022-03-23 06:00 | 44643.25 | 10849.98
2022-03-23 07:00 | 44643.2917 | 11211
2022-03-23 08:00 | 44643.3333 | 11471.91
2022-03-23 09:00 | 44643.375 | 11624.57
2022-03-23 10:00 | 44643.4167 | 11680.01
2022-03-23 11:00 | 44643.4583 | 11525.69
2022-03-23 12:00 | 44643.5 | 11440.99
2022-03-23 13:00 | 44643.5417 | 11318.72
2022-03-23 14:00 | 44643.5833 | 11280.91
2022-03-23 15:00 | 44643.625 | 11332.84
2022-03-23 16:00 | 44643.6667 | 11759.32
2022-03-23 17:00 | 44643.7083 | 11873.59
2022-03-23 18:00 | 44643.75 | 11624.41
2022-03-23 19:00 | 44643.7917 | 11159.47
2022-03-23 20:00 | 44643.8333 | 10805.67
2022-03-23 21:00 | 44643.875 | 10875.18
2022-03-23 22:00 | 44643.9167 | 10638.72
2022-03-23 23:00 | 44643.9583 | 9993.135
2022-03-24 | 44644 | 9138.553
2022-03-24 01:00 | 44644.0417 | 8796.868
2022-03-24 02:00 | 44644.0833 | 8588.776
2022-03-24 03:00 | 44644.125 | 8510.84
2022-03-24 04:00 | 44644.1667 | 8497.936
2022-03-24 05:00 | 44644.2083 | 8696.491
2022-03-24 06:00 | 44644.25 | 9024.79
2022-03-24 07:00 | 44644.2917 | 9442.081
2022-03-24 08:00 | 44644.3333 | 9835.736
2022-03-24 09:00 | 44644.375 | 10077.23
2022-03-24 10:00 | 44644.4167 | 10267.05
2022-03-24 11:00 | 44644.4583 | 10126.44
2022-03-24 12:00 | 44644.5 | 9935.508
2022-03-24 13:00 | 44644.5417 | 9774.36
2022-03-24 14:00 | 44644.5833 | 9730.837
2022-03-24 15:00 | 44644.625 | 9798.773
2022-03-24 16:00 | 44644.6667 | 10230.38
2022-03-24 17:00 | 44644.7083 | 10522.67
2022-03-24 18:00 | 44644.75 | 10519.98
2022-03-24 19:00 | 44644.7917 | 10341.23
2022-03-24 20:00 | 44644.8333 | 10092.97
2022-03-24 21:00 | 44644.875 | 10163.99
2022-03-24 22:00 | 44644.9167 | 10001.81
2022-03-24 23:00 | 44644.9583 | 9503.144
2022-03-25 | 44645 | 8782.685
2022-03-25 01:00 | 44645.0417 | 8365.429
2022-03-25 02:00 | 44645.0833 | 8102.301
2022-03-25 03:00 | 44645.125 | 7944.884
2022-03-25 04:00 | 44645.1667 | 7826.642
2022-03-25 05:00 | 44645.2083 | 7865.889
2022-03-25 06:00 | 44645.25 | 8164.016
2022-03-25 07:00 | 44645.2917 | 8741.706
2022-03-25 08:00 | 44645.3333 | 9302.05
2022-03-25 09:00 | 44645.375 | 9659.587
2022-03-25 10:00 | 44645.4167 | 9927.955
2022-03-25 11:00 | 44645.4583 | 9746.945
2022-03-25 12:00 | 44645.5 | 9445.965
2022-03-25 13:00 | 44645.5417 | 9218.234
2022-03-25 14:00 | 44645.5833 | 9150.662
2022-03-25 15:00 | 44645.625 | 9248.838
2022-03-25 16:00 | 44645.6667 | 9767.115
2022-03-25 17:00 | 44645.7083 | 10212.47
2022-03-25 18:00 | 44645.75 | 10303.39
2022-03-25 19:00 | 44645.7917 | 10206.66
2022-03-25 20:00 | 44645.8333 | 9976.725
2022-03-25 21:00 | 44645.875 | 10014.2
2022-03-25 22:00 | 44645.9167 | 9755.241
2022-03-25 23:00 | 44645.9583 | 9157.53
2022-03-26 | 44646 | 9219.973
2022-03-26 01:00 | 44646.0417 | 8933.659
2022-03-26 02:00 | 44646.0833 | 8834.098
2022-03-26 03:00 | 44646.125 | 8921.291
2022-03-26 04:00 | 44646.1667 | 9417.74
2022-03-26 05:00 | 44646.2083 | 10224.98
2022-03-26 06:00 | 44646.25 | 10811.8
2022-03-26 07:00 | 44646.2917 | 11150.82
2022-03-26 08:00 | 44646.3333 | 11369.19
2022-03-26 09:00 | 44646.375 | 11502.5
2022-03-26 10:00 | 44646.4167 | 11502.62
2022-03-26 11:00 | 44646.4583 | 11352.11
2022-03-26 12:00 | 44646.5 | 11267.4
2022-03-26 13:00 | 44646.5417 | 11161.35
2022-03-26 14:00 | 44646.5833 | 11119.81
2022-03-26 15:00 | 44646.625 | 11168.36
2022-03-26 16:00 | 44646.6667 | 11478.38
2022-03-26 17:00 | 44646.7083 | 11533.72
2022-03-26 18:00 | 44646.75 | 11316.11
2022-03-26 19:00 | 44646.7917 | 10922.14
2022-03-26 20:00 | 44646.8333 | 10678.9
2022-03-26 21:00 | 44646.875 | 10664.97
2022-03-26 22:00 | 44646.9167 | 10344.84
2022-03-26 23:00 | 44646.9583 | 9754.34
2022-03-27 | 44647 | 9109.321
2022-03-27 01:00 | 44647.0417 | 8870.668
2022-03-27 02:00 | 44647.0833 | 8798.717
2022-03-27 03:00 | 44647.125 | 8926.657
2022-03-27 04:00 | 44647.1667 | 9467.823
2022-03-27 05:00 | 44647.2083 | 10246.02
2022-03-27 06:00 | 44647.25 | 10795.5
2022-03-27 07:00 | 44647.2917 | 11124.61
2022-03-27 08:00 | 44647.3333 | 11316.87
2022-03-27 09:00 | 44647.375 | 11441.69
2022-03-27 10:00 | 44647.4167 | 11400.34
2022-03-27 11:00 | 44647.4583 | 11250.68
2022-03-27 12:00 | 44647.5 | 11160.55
2022-03-27 13:00 | 44647.5417 | 11064.71
2022-03-27 14:00 | 44647.5833 | 11018.92
2022-03-27 15:00 | 44647.625 | 11066.2
2022-03-27 16:00 | 44647.6667 | 11287.43
2022-03-27 17:00 | 44647.7083 | 11300.41
2022-03-27 18:00 | 44647.75 | 11115.12
2022-03-27 19:00 | 44647.7917 | 10780.78
2022-03-27 20:00 | 44647.8333 | 10626.63
2022-03-27 21:00 | 44647.875 | 10544.37
2022-03-27 22:00 | 44647.9167 | 10152.42
2022-03-27 23:00 | 44647.9583 | 9600.647
2022-03-28 | 44648 | 8968.045
2022-03-28 01:00 | 44648.0417 | 8768.452
2022-03-28 02:00 | 44648.0833 | 8716.67
2022-03-28 03:00 | 44648.125 | 8884.527
2022-03-28 04:00 | 44648.1667 | 9482.573
2022-03-28 05:00 | 44648.2083 | 10278.92
2022-03-28 06:00 | 44648.25 | 10817.8
2022-03-28 07:00 | 44648.2917 | 11126
2022-03-28 08:00 | 44648.3333 | 11284
2022-03-28 09:00 | 44648.375 | 11389.75
2022-03-28 10:00 | 44648.4167 | 11311.51
2022-03-28 11:00 | 44648.4583 | 11164.83
2022-03-28 12:00 | 44648.5 | 11083.39
2022-03-28 13:00 | 44648.5417 | 11000.3
2022-03-28 14:00 | 44648.5833 | 10953.75
2022-03-28 15:00 | 44648.625 | 10997.49
2022-03-28 16:00 | 44648.6667 | 11153.72
2022-03-28 17:00 | 44648.7083 | 11125.26
2022-03-28 18:00 | 44648.75 | 10937.96
2022-03-28 19:00 | 44648.7917 | 10627.1
2022-03-28 20:00 | 44648.8333 | 10526.27
2022-03-28 21:00 | 44648.875 | 10400.86
2022-03-28 22:00 | 44648.9167 | 9964.682
2022-03-28 23:00 | 44648.9583 | 9439.23
2022-03-29 | 44649 | 8826.526
2022-03-29 01:00 | 44649.0417 | 8671.054
2022-03-29 02:00 | 44649.0833 | 8642.597
2022-03-29 03:00 | 44649.125 | 8851.698
2022-03-29 04:00 | 44649.1667 | 9488.347
2022-03-29 05:00 | 44649.2083 | 10254.73
2022-03-29 06:00 | 44649.25 | 10757.94
2022-03-29 07:00 | 44649.2917 | 11060.15
2022-03-29 08:00 | 44649.3333 | 11195.88
2022-03-29 09:00 | 44649.375 | 11293.96
2022-03-29 10:00 | 44649.4167 | 11178.21
2022-03-29 11:00 | 44649.4583 | 11031.74
2022-03-29 12:00 | 44649.5 | 10943.61
2022-03-29 13:00 | 44649.5417 | 10868.95
2022-03-29 14:00 | 44649.5833 | 10817.99
2022-03-29 15:00 | 44649.625 | 10860.96
2022-03-29 16:00 | 44649.6667 | 10934.68
2022-03-29 17:00 | 44649.7083 | 10868.28
2022-03-29 18:00 | 44649.75 | 10713.06
2022-03-29 19:00 | 44649.7917 | 10459.62
2022-03-29 20:00 | 44649.8333 | 10443.35
2022-03-29 21:00 | 44649.875 | 10252.76
2022-03-29 22:00 | 44649.9167 | 9747.23
2022-03-29 23:00 | 44649.9583 | 9256.998
2022-03-30 | 44650 | 8653.894
2022-03-30 01:00 | 44650.0417 | 8529.806
2022-03-30 02:00 | 44650.0833 | 8518.689
2022-03-30 03:00 | 44650.125 | 8762.246
2022-03-30 04:00 | 44650.1667 | 9456.572
2022-03-30 05:00 | 44650.2083 | 10248.02
2022-03-30 06:00 | 44650.25 | 10747.8
2022-03-30 07:00 | 44650.2917 | 11033.5
2022-03-30 08:00 | 44650.3333 | 11140.27
2022-03-30 09:00 | 44650.375 | 11222.14
2022-03-30 10:00 | 44650.4167 | 11073.2
2022-03-30 11:00 | 44650.4583 | 10928.37
2022-03-30 12:00 | 44650.5 | 10847.99
2022-03-30 13:00 | 44650.5417 | 10783.83
2022-03-30 14:00 | 44650.5833 | 10731.82
2022-03-30 15:00 | 44650.625 | 10771.86
2022-03-30 16:00 | 44650.6667 | 10790.84
2022-03-30 17:00 | 44650.7083 | 10687.67
2022-03-30 18:00 | 44650.75 | 10527.49
2022-03-30 19:00 | 44650.7917 | 10290.16
2022-03-30 20:00 | 44650.8333 | 10317.88
2022-03-30 21:00 | 44650.875 | 10089.69
2022-03-30 22:00 | 44650.9167 | 9543.177
2022-03-30 23:00 | 44650.9583 | 9071.038
2022-03-31 | 44651 | 8071.418
2022-03-31 01:00 | 44651.0417 | 7918.058
2022-03-31 02:00 | 44651.0833 | 7869.136
2022-03-31 03:00 | 44651.125 | 7919.032
2022-03-31 04:00 | 44651.1667 | 8187.475
2022-03-31 05:00 | 44651.2083 | 8484.112
2022-03-31 06:00 | 44651.25 | 8756.437
2022-03-31 07:00 | 44651.2917 | 9089.132
2022-03-31 08:00 | 44651.3333 | 9323.054
2022-03-31 09:00 | 44651.375 | 9471.313
2022-03-31 10:00 | 44651.4167 | 9471.445
2022-03-31 11:00 | 44651.4583 | 9352.558
2022-03-31 12:00 | 44651.5 | 9192.966
2022-03-31 13:00 | 44651.5417 | 9090.775
2022-03-31 14:00 | 44651.5833 | 9039.63
2022-03-31 15:00 | 44651.625 | 9092.224
2022-03-31 16:00 | 44651.6667 | 9193.105
2022-03-31 17:00 | 44651.7083 | 9273.771
2022-03-31 18:00 | 44651.75 | 9307.001
2022-03-31 19:00 | 44651.7917 | 9240.042
2022-03-31 20:00 | 44651.8333 | 9273.912
2022-03-31 21:00 | 44651.875 | 9114.442
2022-03-31 22:00 | 44651.9167 | 8708.037
2022-03-31 23:00 | 44651.9583 | 8334.739

## 2.3 Market response
2.3 Market response
Results from the market response study as performed by E-Cube were presented on the TF iSR of 8 July 2020.
Compared to last year the volume has considerably increased due to the inclusion of Nord Pool, the inclusion of complex bids as well as a higher volulme on EPEX
Concerning the evolution of the volume of Market Response, two growth rate trajectories were proposed:
A growth rate of 6% based on observation of the last three years
A growth rate of 8% based on observation of the whole data set
While taking into account the opinion of the different stakeholders and considering the various efforts on smart meter roll-out, the Internet Of Energy as well as the Transfer Of Energy projects, it is believed that the growing trend will continue.
Elia proposes hence to take 7% into account for the Strategic Reserve 2021-22 which is line with the 7% used in the 2020-21 Strategic Reserve study.
Market response volume per winter | [5 empty] | Market response categories & constraints
Market Response volume [MW] | Measured | Extrapolation |  |  |  | Categories & Constraints | Distribution [%]
|  |  | Winters under consideration |  |  | Max use of 1 hour | 10
| 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | Max use of 2 hours | 35
7% growth | 1041 | 1113.87 | 1191.8409 | 1275.2698 | 1364.5386 | Max use of 4 hours | 10
[6 empty] | Max use of 8 hours | 30
[6 empty] | No limit | 15

## 3. Balancing reserves
3. Balancing reserves
Volume of balancing reserves assumed to be provided by Belgian production units [MW]
| 2020-21 | 2021-22 | 2022-23 | 2023-24
FCR | 0 | 0 | 0 | 0
aFRR | 150 | 152 | 151.2 | 149.88
mFRR | 419.5 | 406.21 | 397.92 | 389.63
Total | 569.5 | 558.21 | 549.12 | 539.51

## 4. Flow based domains
4. Flow-based domains
Elia has developed a flow-based framework which does not rely on historical domains, but instead aims to mimic the operational flow-based capacity calculation workflow.
The framework is based on a zonal model of Europe, the grid model used is based on the TYNDP 2020.
The flow-based perimeter is now in CORE*, the degree of complexity has increased and the domains have now shape 13 dimensions.
Using a framework allows hence to consult on the parameters rather than domains.
The flow-based domains will be illustrated in the final report.
For more information on flow-based modelling, please refer to the public consultation on methodology:
https://www.elia.be/en/public-consultation/20200603_public-consultation-on-the-methodology-of-volumes-of-strategic-reserve-for-winter-2021-2022
* note that the framework has been improved to be able to cope with CORE and not CORE-MOD
Market Parameters |  | 2021 | 2022 | 2023
Flow-based perimeter |  | CORE | CORE | CORE
Bidding zones |  | As is | As is | As is
minRAM |  | see table | see table | see table
Treatment of external flows |  | Standard Hybrid Coupling | Standard Hybrid Coupling | Standard Hybrid Coupling
External constraints |  | BE: -6500 | BE: -7500 | BE: -7500
|  | NL: -6500 | NL: -6500 | NL: -6500
|  | NL: +6500 | NL: +6500 | NL: +6500
CNEC selection |  | XB + int > 5% | XB + int > 5% | XB | A 5% threshold (meaning the CNEC is at least 5% sensitive to a net position change of any of the CCR bidding zones)
Use of PST in capacity calculation |  | BE: 1/2 | BE: 1/2 | BE: 1/2
|  | Other: 1/3 | Other: 1/3 | Other: 1/3
Use of PST in capacity allocation (flex in market) |  | - | - | -
Use of HVDC in capacity calculation |  | - | - | -
Use of HVDC in capacity allocation (flex in market) |  | Only Alegro | Only Alegro | Only Alegro
MinRAM trajectories in %
Country | 2020 | 2021 | 2022 | 2023 | Justification
Netherlands | 28 | 37 | 45 | 53 | Action plan for most constraining XB CNEC
Belgium* | 70 | 70 | 70 | 70 | *with application of derogation
Germany | 21.3 | 31 | 40.8 | 50.5 | Action plan
France | 70 | 70 | 70 | 70
Slovenia | 70 | 70 | 70 | 70
Hungary | 70 | 70 | 70 | 70
Kroatia | 70 | 70 | 70 | 70
Romania | 70 | 70 | 70 | 70
Czechia | 70 | 70 | 70 | 70
Austria | 70 | 70 | 70 | 70
Slovakia | 70 | 70 | 70 | 70
Poland | 70 | 70 | 70 | 70