## Contents
Adequacy and Flexibility study 2022-2032 - 'CENTRAL' scenario data for Belgium
This data is provided in the framework of the Adequacy and Flexibility study covering the years from 2022 to 2032 published end June 2021.
It includes data assumptions for Belgium from 2022 to 2032.
This Excel file contains the data related to the scenario framework of the study including economic and flexibility aspects.
This Excel file is provided as complemented to the study report.
Input data for market and flexibility simulations
1. Generation
1.1. Invidividually modelled thermal generation
1.2. Renewable energy sources and non-CIPU thermal units
1.3. Storage
2. Demand
2.1. Total electricity demand
2.2. Demand Side Response
3. Economic and technical variables
3.1. Fuel and CO2 prices
3.2. Investment costs
3.3. Outages
3.4. Flexibility characteristics

## 1.1. Ind. mod. thermal prod.
1.1. Individually modelled thermal generation
Situation at end of the given year - considered as available for the EVA/market
Owner | Production unit name | Type | Fuel type | Net generation capacity [MW] | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Engie electrabel | Syral Aalst GT | CHP | Gas | 43 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie electrabel | Syral Aalst ST | CHP | Gas | 5 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie electrabel | AALTER TJ | TJ | Oil | 18 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie electrabel | AMERCOEUR 1R GT | CCGT-GT | Gas | 289 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie electrabel | AMERCOEUR 1R ST_cur | CCGT-ST | Gas | 162 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Luminus | EDF Luminus Angleur GT41 | GT | Gas | 64 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Luminus | EDF Luminus Angleur GT42 | GT | Gas | 64 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Luminus | EDF Luminus Angleur GT31 | CCGT-GT | Gas | 25 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Luminus | EDF Luminus Angleur GT32 | CCGT-GT | Gas | 25 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie electrabel | AWIRS 4 | CL | Biomass | 75 | bar: Situation at end of the given year - considered as available for the EVA/market 2020 to Situation at end of the given year - considered as available for the EVA/market 2032
Engie electrabel | BEERSE TJ | TJ | Oil | 32 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Indaver | Beveren 2 Indaver | IS | Waste | 21 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie electrabel | Beveren Ineos Phenol Chem | CHP | Gas | 25.1 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Indaver | Beveren Sleco | IS | Waste | 41 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Biostoom | Biostoom Oostende | IS | Waste | 19.4 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie electrabel | CIERREUX TJ | TJ | Oil | 18 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie electrabel | DOEL 1 | NU | Nuclear | 445 | yes | yes | yes | yes | yes | no | no | no | no | no | no | no | no
Engie electrabel | DOEL 2 | NU | Nuclear | 445 | yes | yes | yes | yes | yes | no | no | no | no | no | no | no | no
Engie electrabel | DOEL 3 | NU | Nuclear | 1006 | yes | yes | no | no | no | no | no | no | no | no | no | no | no
Engie electrabel | DOEL 4 | NU | Nuclear | 1039 | yes | yes | yes | yes | yes | no | no | no | no | no | no | no | no
Engie electrabel | DROGENBOS GT1 | CCGT-GT | Gas | 150 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie electrabel | DROGENBOS GT2 | CCGT-GT | Gas | 150 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie electrabel | DROGENBOS ST | CCGT-ST | Gas | 160 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Euro-silo | Euro-Silo | CHP | Gas | 12.9 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Green Power | Greenpower Oostende | CHP | Waste | 20 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Luminus | EDF Luminus Ham GT31 | GT | Gas | 58 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Luminus | EDF Luminus Ham GT32 | GT | Gas | 58 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Luminus | EDF Luminus Ham STEG | CCGT | Gas | 39 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie electrabel | HERDERSBRUG GT1 | CCGT-GT | Gas | 157 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie electrabel | HERDERSBRUG GT2 | CCGT-GT | Gas | 156.3 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie electrabel | HERDERSBRUG ST | CCGT-ST | Gas | 167 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
IPALLE | Ipalle Thumaide | IS | Waste | 34 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Indaver | Beveren 3 Indaver | IS | Waste | 24 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
INEOS | INESCO GT1 | CHP | Gas | 44.8 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
INEOS | INESCO GT2 | CHP | Gas | 44.8 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
INEOS | INESCO ST | CHP | Gas | 48.5 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
INTRADEL | Intradel Herstal IS | IS | Waste | 32 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
IVBO | IVBO | IS | Waste | 16 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Luminus | IZEGEM | CHP | Gas | 20 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Inovyn | Jemeppe-sur-Sambre GT1 | CHP | Gas | 48 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Inovyn | Jemeppe-sur-Sambre GT2 | CHP | Gas | 48 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Inovyn | Jemeppe-sur-Sambre ST | CHP | Gas | 10 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie electrabel | Sappi Lanaken GT | CHP | Gas | 43 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
STORA | STORA LANGERBRUGGE WKK1 | CHP | Biomass | 10 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
STORA | STORA LANGERBRUGGE WKK2 | CHP | Biomass | 40 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Lillo Energy | Lillo Degussa GT1 | CHP | Gas | 43 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Lillo Energy | Lillo Degussa GT2 | CHP | Gas | 32 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Lillo Energy | Lillo Degussa ST | CHP | Gas | 10 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Direct Energie | Marcinelle Energie TGV | CCGT | Gas | 413 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie electrabel | Oorderen Bayer | CHP | Gas | 43 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie electrabel | Monsanto Lillo WKK EBL | CHP | Gas | 43 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Luminus | EDF Luminus Ringvaart STEG | CCGT | Gas | 385 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie electrabel | RODENHUIZE 4 | CL | Biomass | 205 | yes | yes | yes | no | no | no | no | no | no | no | no | no | no
Engie electrabel | SAINT-GHISLAIN STEG | CCGT | Gas | 350 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
EXXONMOBIL | Scheldelaan Exxonmobil | CHP | Gas | 140 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Luminus | EDF Luminus Seraing GT1 | CCGT-GT | Gas | 150 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Luminus | EDF Luminus Seraing GT2 | CCGT-GT | Gas | 150 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Luminus | EDF Luminus Seraing TGV | CCGT-ST | Gas | 170 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
TAMINCO | TAMINCO Gent WKK | CHP | Gas | 6.3 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie electrabel | TIHANGE 1N | NU | Nuclear | 481 | yes | yes | yes | yes | yes | no | no | no | no | no | no | no | no
Engie electrabel | TIHANGE 1S | NU | Nuclear | 481 | yes | yes | yes | yes | yes | no | no | no | no | no | no | no | no
Engie electrabel | TIHANGE 2 | NU | Nuclear | 1008 | yes | yes | yes | no | no | no | no | no | no | no | no | no | no
Engie electrabel | TIHANGE 3 | NU | Nuclear | 1038 | yes | yes | yes | yes | yes | no | no | no | no | no | no | no | no
T-Power | T-Power | CCGT | Gas | 425 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie electrabel | Vilvoorde GT | CCGT-GT | Gas | 255 | yes | yes | yes | yes | yes | no | no | no | no | no | no | no | no
Engie electrabel | Vilvoorde ST | CCGT-ST | Gas | 105 | no | yes | yes | no | no | no | no | no | no | no | no | no | no
TOTAL | Wilmarsdonk Total GT1 | CHP | Gas | 43 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
TOTAL | Wilmarsdonk Total GT2 | CHP | Gas | 43 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
TOTAL | Wilmarsdonk Total GT3 | CHP | Gas | 43 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Zandvliet Power NV | Zandvliet Power | CCGT | Gas | 386.2 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie electrabel | Zedelgem TJ | TJ | Oil | 18 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie electrabel | Fluxys LNG Zeebrugge WKK | CHP | Gas | 40 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie electrabel | Zeebrugge TJ | TJ | Oil | 18 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie electrabel | Zelzate 2 Knippegroen | CCGT | Gas | 305 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie electrabel | Zelzate TJ | TJ | Oil | 18 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie electrabel | Zwijndrecht Lanxess GT | CHP | Gas | 43 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie electrabel | Zwijndrecht Lanxess ST | CHP | Gas | 15 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie electrabel | ISVAG | IS | Waste | 12 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie electrabel | NOORDSCHOTE TJ | TJ | Oil | 18 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie electrabel | SCHAERBEEK SIOMAB ST1 | IS | Waste | 15 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie electrabel | SCHAERBEEK SIOMAB ST2 | IS | Waste | 15 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie electrabel | SCHAERBEEK SIOMAB ST3 | IS | Waste | 15 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Biopower | Biomassa Oostende | IS | Biomass | 18 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie electrabel | TURBOJET VOLTA | TJ | Oil | 18 | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Borealis | Borealis Kallo Cogen GT_ST | CHP | Gas | 32 | no | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Indaver | E-wood | IS | Waste | 22 | no | no | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Legend Unit-Type
CCGT | Combined Cycle
CCGT-GT | Combined Cycle - Gas Turbine
CCGT-ST | Combined Cycle - Steam Turbine
CL | Classic
GT | Gas Turbine
ST | Steam Turbine
IS | Incineration Station
NU | Nuclear
TJ | TurboJet
CHP | Cogeneration Unit

## 1.2. Renewable and non-CIPU
1.2. Evolution of renewable energy sources and non-CIPU thermal units
Generation capacity at the end of the mentioned year [MW]
Generation type |  | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
| Wind | 3876 | 4599 | 4979.21 | 5234.42 | 5489.63 | 5744.84 | 6000 | 6931 | 7161 | 8839 | 9069 | 9300 | 9531 | 9761
| Wind onshore | 2320 | 2471 | 2726.21 | 2981.42 | 3236.63 | 3491.84 | 3747 | 3978 | 4208 | 4439 | 4669 | 4900 | 5131 | 5361
| Wind offshore | 1556 | 2253 | 2253 | 2253 | 2253 | 2253 | 2253 | 2953 | 2953 | 4400 | 4400 | 4400 | 4400 | 4400
| Photovoltaics | 4550 | 4788 | 5430.4 | 6072.8 | 6715.2 | 7357.6 | 8000 | 8600 | 9200 | 9800 | 10400 | 11000 | 11600 | 12200
| Hydro RoR | 117 | 117 | 121 | 125 | 129 | 133 | 137 | 139.8 | 142.6 | 145.4 | 148.2 | 151 | 153.8 | 156.6
| Gas CHP - non-CIPU | 1206 | 1297 | 1379 | 1379 | 1379 | 1379 | 1379 | 1379 | 1379 | 1379 | 1379 | 1379 | 1379 | 1379
| Biomass - non-CIPU | 446 | 504.4 | 504 | 504 | 504 | 504 | 504 | 504 | 504 | 504 | 504 | 504 | 504 | 504
| Waste - non-CIPU | 51 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46

## 1.3. Storage
1.3. Storage
1.3.1. Pumped-storage
Voulme at the end of the mentioned year[MW]
|  |  | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
| Capacity [MW] | Pumped-storage | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224
| Reservoir volume [MWh] | Storage reservoir derating (ancillary services) [MWh] | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
|  | Available storage for economical dispatch | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300
1.3.2. Other storage facilities
Capacity and volume of storage at the end of the mentioned year[MW] or [MWh]
|  |  | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
| Total capacity [MW] |  | 25.5 | 25.5 | 103.1 | 164.1 | 278.9 | 441.5 | 589.6 | 756.7 | 943 | 1148.4 | 1372.9 | 1600 | 1600 | 1600
| Capacity [MW] | Large scale storage ("in-the-market") | 25.5 | 25.5 | 72 | 97 | 171 | 288 | 382 | 411.8 | 457.8 | 519.8 | 597.9 | 675.7 | 675.7 | 675.7
|  | Small scale storage ("out-of-market") | 0 | 0 | 29 | 60.8 | 95.3 | 132.5 | 172.5 | 215.5 | 261.5 | 310.5 | 362.5 | 417.5 | 417.5 | 417.5
|  | Vehicule-to-Grid (V2G) | 0 | 0 | 2.1 | 6.3 | 12.6 | 21 | 35 | 129.4 | 223.7 | 318.1 | 412.4 | 506.8 | 506.8 | 506.8
|  | V2G "in-the-market" | 0 | 0 | 0 | 0.1 | 0.4 | 0.8 | 1.8 | 18.1 | 51.5 | 101.8 | 169.1 | 253.4 | 253.4 | 253.4
|  | V2G "out-of-market" | 0 | 0 | 2.1 | 6.2 | 12.2 | 20.2 | 33.3 | 111.2 | 172.3 | 216.3 | 243.3 | 253.4 | 253.4 | 253.4
| Reservoir volume [MWh] | Large scale storage ("in-the-market") | 51 | 51 | 144 | 194 | 342 | 576 | 764 | 823.6 | 915.6 | 1039.6 | 1195.8 | 1351.4 | 1351.4 | 1351.4
| Reservoir volume [MWh] | Small scale storage ("out-of-market") | 0 | 0 | 87 | 182.3 | 285.9 | 397.6 | 517.6 | 646.6 | 784.6 | 931.6 | 1087.6 | 1252.6 | 1252.6 | 1252.6
|  | Vehicule-to-grid | 0 | 0 | 8.4 | 25.2 | 50.4 | 84 | 140 | 517.4 | 894.9 | 1272.3 | 1649.8 | 2027.2 | 2027.2 | 2027.2
|  | V2G "in-the-market" | 0 | 0 | 0.1 | 0.5 | 1.5 | 3.4 | 7 | 72.4 | 205.8 | 407.1 | 676.4 | 1013.6 | 1013.6 | 1013.6
|  | V2G "out-of-market" | 0 | 0 | 8.3 | 24.7 | 48.9 | 80.6 | 133 | 445 | 689.1 | 865.2 | 973.4 | 1013.6 | 1013.6 | 1013.6

## 2.1. Tot. elec. demand
2.1. Total electricity consumption
| Year | Historical* normalised total demand [TWh] | Normalized total demand with WEM electrification [TWh] | Normalized total demand with WAM electrification [TWh] | Normalized total demand - CENTRAL [TWh]
historical | 2019 | 85.7 | 85.7 | 85.7 | 85.7
| 2020 | 82 |  |  | 82
| 2021 |  | 85 | 85.7 | 85
| 2022 |  | 86.8 | 87.6 | 86.8
| 2023 |  | 87.5 | 88.6 | 87.5
| 2024 |  | 88.2 | 89.5 | 88.2
| 2025 |  | 88.9 | 90.3 | 88.9
| 2026 |  | 89.8 | 91.4 | 90.2
| 2027 |  | 90.7 | 92.5 | 91.5
| 2028 |  | 91.6 | 93.5 | 92.8
| 2029 |  | 92.3 | 94.4 | 94.1
| 2030 |  | 93 | 95.3 | 95.3
| 2031 |  | 93.4 | 95.9 | 95.9
| 2032 |  | 93.7 | 96.5 | 96.5
* The historical total demand is based on the current estimation of Elia for the total load (without Twinerg/Sotel and including losses) on which normalisation was applied. The 2020 value is an estimation.
2.1.1. Electrification of the transport sector
The equivalent number of electric vehicles (EVs) assumed in the final NECP for WEM and WAM scenarios (in Mio) are estimated by assuming 17KWh/100km and 15.000 km/year.
| Year |  | Estimated # EV in WEM | Estimated # EV in WAM | Estimated # EV in CENTRAL
| 2021 |  | 0.07 | 0.32 | 0.07
| 2022 |  | 0.1 | 0.42 | 0.1
| 2023 |  | 0.13 | 0.52 | 0.13
| 2024 |  | 0.16 | 0.62 | 0.16
| 2025 |  | 0.2 | 0.72 | 0.2
| 2026 |  | 0.27 | 0.87 | 0.45
| 2027 |  | 0.35 | 1.01 | 0.7
| 2028 |  | 0.42 | 1.16 | 0.95
| 2029 |  | 0.49 | 1.3 | 1.2
| 2030 |  | 0.57 | 1.44 | 1.44
| 2031 |  | 0.65 | 1.6 | 1.6
| 2032 |  | 0.75 | 1.78 | 1.78
2.1.2. Electrification of heating
The equivalent penetration of heat pumps (HPs) assumed in the final NECP for WEM and WAM scenarios.
| Year |  | Estimated penetration HP in WEM | Estimated penetration HP in WAM | Estimated penetration HP in CENTRAL
| 2021 |  | 0.88% | 0.98% | 0.88%
| 2022 |  | 1.01% | 1.19% | 1.01%
| 2023 |  | 1.15% | 1.41% | 1.15%
| 2024 |  | 1.29% | 1.62% | 1.29%
| 2025 |  | 1.42% | 1.84% | 1.42%
| 2026 |  | 1.59% | 2.19% | 1.86%
| 2027 |  | 1.76% | 2.55% | 2.3%
| 2028 |  | 1.93% | 2.9% | 2.74%
| 2029 |  | 2.1% | 3.26% | 3.18%
| 2030 |  | 2.27% | 3.62% | 3.62%
| 2031 |  | 2.45% | 4.01% | 4.01%
| 2032 |  | 2.65% | 4.45% | 4.45%

## 2.2. Demand Side Response
2.2. Demand Side Response
Demand Side Response volume per year
Voulme at the end of the mentioned year[MW]
| 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Total shedding capacity (including the ones participating to the ancillary services) | 1448 | 1521 | 1599 | 1682 | 1772 | 1863 | 1953 | 2044 | 2135 | 2226 | 2316 | 2407 | 2407 | 2407
Max use of 1 hour | 104 | 111 | 119 | 128 | 137 | 146 | 155 | 164 | 173 | 182 | 191 | 200 | 200 | 200
Max use of 2 hours | 365 | 390 | 417 | 446 | 478 | 509 | 541 | 573 | 605 | 636 | 668 | 700 | 700 | 700
Max use of 4 hours* | 511 | 519 | 526 | 534 | 543 | 553 | 561 | 571 | 580 | 589 | 598 | 607 | 607 | 607
Max use of 8 hours | 312 | 334 | 358 | 383 | 409 | 437 | 464 | 491 | 518 | 546 | 573 | 600 | 600 | 600
No limit | 156 | 167 | 179 | 191 | 205 | 218 | 232 | 245 | 259 | 273 | 286 | 300 | 300 | 300
* The volume for ancillary services is included in the "max use of 4 hours" category
Voulme at the end of the mentioned year [GWh/day in winter period]
| 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Total shifting capacity [GWh/day in winter period] | 0 | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.7 | 0.9 | 1.1 | 1.3 | 1.5 | 1.5 | 1.5

## 3.1. Fuel and CO2 prices
3.1. Fuel and CO2 prices
Fuel and CO2 prices per year
Source: IEA - World Energy Outlook 2020 (WEO)
https://www.iea.org/topics/world-energy-outlook
Price in [€2019] | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | Source
Gas TTF [€/GJ] | 4.8 | 4.8 | 4.8 | 5.7 | 5.8 | 5.9 | 6.1 | 6.2 | 6.3 | 6.4 | 6.5 | WEO2020-stated policies scenarios (STEPS)
Coal ARA [€/GJ] | 2.35 | 2.35 | 2.35 | 2.35 | 2.39 | 2.42 | 2.46 | 2.49 | 2.53 | 2.52 | 2.51 | WEO2020-stated policies scenarios (STEPS)
Oil [€/GJ] | 9.7 | 9.9 | 10.1 | 10.3 | 10.5 | 10.6 | 10.8 | 10.9 | 11.1 | 11.2 | 11.3 | WEO2020-stated policies scenarios (STEPS)
CO2 EUA [€/tCO2] - 'CENTRAL' scenario | 40 | 40 | 40 | 43.2 | 46 | 48.8 | 51.6 | 54.4 | 57.3 | 60.1 | 62.9 | Forward price beginning of March' 21 for 2022, 2023 and 2024. From 2025, average of the IEA-WEO2020 SDS (Sustainable Development Scenario) and STEPS (Stated Policies Scenario) scenarios

## 3.2. Investment costs
3.2. Economic assumptions
All prices are assumed to be in €2019.
The industry wide reference WACC proposed for this study is 5.53%. In addition, as specified in the Economic viability metric methodology (see study report), a technology specific hurdle premium was added. The hurdle rate is shown on the table.
Sources behind the data are included in the study report.
Technologies part of the structural block (economic viability assessment) |  | Applies to | CAPEX [€/kW] | FOM (including major overhauls) [€/kW/y] | Investment economic lifetime [years] | Hurdle rate in EOM (WACC + premium)
Existing (assumed no extension costs) | CCGT | Existing units <25 years | - | 30 | - | 7%
| OCGT |  | - | 20 | - | 8%
| CHP | All existing capacity | - | 60 | - | 7%
| Turbojets | All existing capacity | - | 30 | - | 8%
| Demand Response | All existing capacity in 2020 | - | 10 | - | 9%
| Pumped Storage | All existing capacity | - | 30 | - | 9%
Existing (assuming extension costs needed) | CCGT | Existing units >25 years | 100 | 30 | 15 | 9.5%
| OCGT |  | 80 | 40 | 15 | 11%
New | Diesels | New capacity | 300 | 15 | 15 | 14%
| Gas engines | New capacity | 400 | 15 | 15 | 14%
| CCGT | >800 MW | 600 | 25 | 20 | 12%
|  | 400 < 800 MW | 750 | 30 | 20 | 12%
|  | < 400 MW | 850 | 30 | 20 | 12%
| OCGT | >100 MW | 400 | 20 | 20 | 14%
|  | <100 MW | 500 | 20 | 20 | 14%
| CHP | New capacity | 800 | 60 | 20 | 12%
| Demand Side Response | New capacity 0 < 500 MW | All costs included in the FOM | 20 | - | 14%
|  | New capacity 500 < 1000 MW |  | 40 | - | 14%
|  | New capacity 1000 < 1500 MW |  | 60 | - | 14%
|  | New capacity 1500 < 2000 MW |  | 80 | - | 14%
| Batteries/Storage | Large scale batteries | 100 | 10 | 10 | 14%
|  | Enabling new V2G | 130 | 10 | 10 | 14%
| Pumped Storage - new unit | New unit in Coo | 900 | 30 | 25 | 14%

## 3.3. Outages
3.3. Outages
3.3.1. Forced outage rates
For the generation technologies, these numbers have been calculated from the last 10 years available data (from 2011 up to and including 2020). These data come from the ENTSO-E transparency platform (ETP: https://transparency.entsoe.eu/) and from Elia’s internal database.
The public data from ENTSO-E Transparency Data is used for historical data when available (i.e. from 2015 up to and including 2020).
Forced outage parameters (over 2011-2020)
Category | Number of FO per year | Average FO rate [%] | Average duration of FO rate [hours]
Nuclear | 1.6 | 3.73% | 240 hours (around 10 days)
CCGT | 7 | 8.38% | 101 hours (around 4 days)
GT | 3.1 | 9.22% | 201 hours (around 8 days)
TJ | 2 | 3.58% | 98 hours (around 4 days)
Waste | 1.5 | 1.02% | 82 hours (around 3 days)
CHP | 3.8 | 7.01% | 124 hours (around 5 days)
Pumped storage | 3 | 4.5% | 181 hours (around 8 days)
DC links (in each direction) | 2 | 6% | 168 hours (around 7 days)
3.3.2. Planned outages
The latest public information (REMIT) regarding the planned outages is used
For years were no data are available in REMIT, the data from ENTSO-E is used : https://www.entsoe.eu/outlooks/midterm/

## 3.4. Flex. charact.
3.4. Flexibility characteristics
| Parameters | [8 empty] | Maximum upward flexibility |  |  | Maximim downward flexibility |  |  | Energy Limit | Clarification, justifications and remarks
Parameter | Minimum up time | Minimum down time | Hot start up time | Warm start up time | Cold start up time | Transition time from "hot" to "warm" | Transition time from "warm" to "cold" | Min Stable power | Ramp Rate | Ramping flexibility limit | Fast flexibility limit | Slow flexibility limit | Ramping flexibility limit | Fast flexibility limit | Slow flexibility limit
Definition | Duration that a unit needs to remain in "on" status after the start of an activation | Duration that a unit needs to remain in "off" status after the end of an activation | Duration between the activation signal and attaining minimum stable power in "hot", "warm" or "cold" conditions |  |  | Duration that a unit goes from "hot" to "warm" status after the end of an activation | Duration that a unit goes from "warm" to "cold" status after the end of an activation | Minimum power output level when in "on" status | Minimum power variation in a time period | Maximum share of the installed capacity which can participate in the categories upward ramping, fast and slow flex (without accounting other constraints, e.g. ramp rate) |  |  | Maximum share of the installed capacity which can participate in the categories downward ramping, fast and slow flex (without accounting other constraints, e.g. ramp rate) |  |  | expressed in number of hours during which the plant can product at its maximum capacity
Unit | hours | hours | hours | hours | hours | hours | hours | % Pmax | %Pmax/min | %Pmax | %Pmax | %Pmax | %Pmax | %Pmax | %Pmax | hours
Nuclear
Interconnections (AC & DC) | [9 empty] | min(ATC import -Pnom import; 100) | min(ATC import -Pnom import; 350) | ATC import-Pnom import | min(ATCexport - Pnom export;100) | min(ATCexport - Pnom export;350) | ATCexport - Pnom export |  | Flexibility is constrained by the remaining import / export capacity after day-ahead. Additional constraints may be implemented by * the availability of the cross-border energy service, particularly during high (reduced upward flexibility) / low price periods (reduced downward flexibility) *future balancing market liquidity on European platforms *legal and regulatory limits (cf. Art. 157 of SOGL)
Renewable Generation
Wind offshore | [8 empty] | 100% |  |  |  | 65%Pnom | 65% Pnom | 65% Pom |  | Based on literature [1] and further constrained based on an analysis of day-ahead forecast errors. Ramping flexibility limited to 400 MW and 925 MW (as from 2028)
Wind onshore (only share CIPU) | [8 empty] | 100% |  |  |  |  | 88% Pnom | 88% Pnom |  | Based on literature [1] and further constrained based on an analysis of day-ahead forecast errors
Solar (only share CIPU) | [8 empty] | 100% |  |  |  |  | 90% Pnom | 90% Pnom |  | Based on return on experience, and analysis of day-ahead forecast errors
Run-of-River Hydro
Biofuel (only share CIPU) | 8h | 8h | 3h | 5h | 7h | 12h | 72h | 40% | 3% |  |  |  | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") |  | Based on literature [2] and CHP recent steam turbine values
CCGT
new (to be commissioned) | 2h | 2h | 1h | 1.5h | 2h | 8h | 48h | 30% | 11% | Pmax-Pnom (0% when "off") | Pmax-Pnom (0% when "off") | Pmax-Pnom (100% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") |  | Based on literature [3] and [4]
recent (commissioned after 2000) | 3h | 3h | 1.5h | 2h | 3h | 8h | 48h | 40% | 6% | Pmax-Pnom (0% when "off") | Pmax-Pnom (0% when "off") | Pmax-Pnom (100% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off")
old (commissioned before 2000) | 3h | 3h | 1.5h | 2,5h | 4h | 8h | 48h | 45% | 3% | Pmax-Pnom (0% when "off") | Pmax-Pnom (0% when "off") | Pmax-Pnom (100% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off")
OCGT
new | 1h | 1h | 0.16h | 0.16h | 0.16h | 2h | 3h | 20% | 15% | Pmax-Pnom (0% when "off") | Pmax-Pnom (100% when "off") | Pmax-Pnom (100% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") |  | Based on literature [3] and [4]
existing | 1h | 1h | 0.16h | 0.16h | 0.16h | 2h | 3h | 30% | 12% | Pmax-Pnom (0% when "off") | Pmax-Pnom (100% when "off") | Pmax-Pnom (100% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off")
CHP (GAS TURBINE) | 4h | 4h | 1h | 1h | 4h | 2 h | 3 h | 50% | 10% |  |  |  | Pnom-Pmin | Pnom-Pmin | Pnom-Pmin | 8 hours | Based on literature [3] and CHP recent steam turbine values (+ [5] for energy limit) + input COGEN
CHP (CCGT) | 3h | 3h | 1h | 2h | 3h | 8h | 48h | 40% | 6% | Pmax-Pnom | Pmax-Pnom | Pmax-Pnom | Pnom-Pmin | Pnom-Pmin | Pnom-Pmin |  | Based on literature [3] and CHP recent steam turbine values (+ [5] for energy limit) + input COGEN
Pumped Storage | [8 empty] | 100% | Pmax- Pnom (0% when "off") | Pmax - Pnom | Pmax - Pnom | Pnom- Pmax- (0% when "off") | Pnom - Pmax- | Pnom - Pmax- | 4,5 hours | Aggregation of PHS-sites. Based on literature review [6; 7] and Elia's internal information
Demand Response
CAT-4h | [8 empty] | 100% | min (10% Pmax ; Pmax - Pnom) | min (40% Pmax ; Pmax - Pnom) | Pmax - Pnom |  |  |  | 1, 2 , 4, 8 hours - no limit | Based on E-Cube study and and Elia's estimation [9]
New technologies
Small scale storage | [8 empty] | 100% | Pmax-Pnom | Pmax-Pnom | Pmax-Pnom | Pnom - Pmax- | Pnom - Pmax- | Pnom - Pmax- | 3 hours | Based on literature review [9;10;11], Elia's best estimate
Large scale storage | [8 empty] | 100% | Pmax-Pnom | Pmax-Pnom | Pmax-Pnom | Pnom - Pmax- | Pnom - Pmax- | Pnom - Pmax- | 1 hours
Consumption shifting | [8 empty] | 100% | Pmax-Pnom | Pmax-Pnom | Pmax-Pnom
Vehicle to Grid (V2G) | [8 empty] | 100% | Pmax-Pnom | Pmax-Pnom | Pmax-Pnom | Pnom - Pmax- | Pnom - Pmax- | Pnom - Pmax- | 3 hours
Electrolyzers | [8 empty] | 100% |  | Pnom (0% when "off") | Pnom (0% when "off") |  |  |  |  | Based on literature [12]
Diesel + Turbojets | 0 h | 0.10 h | 0.05 h | 0.05 h | 0.05 h | 0 | 0 | 30% | 100% | Pmax-Pnom (0% when "off") | Pmax-Pnom (100% when "off") | Pmax-Pnom (100% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") |  | Based on Internal Combustion Engines [13]
Terminology
Pmax | Maximum injected power of the unit (MW)
Pmax- | Maximum absorbed power of the unit (MW), i.e. negative value
Pnom | Day-Ahead Scheduled power of the unit (MW), i.e. positive or negative value
Pmin | Minimum stable power (MW)
ATCexport | Maximum available export capacity (MW)
ATCimport | Maximum available import capacity (MW)
ramping flex | Capacity which can be regulated continuously up- or downward in a timeframe of one minute
fast flex | Capacity which can be regulated up- or downward in a time frame of 15 minutes
slow flew | Capacity which can be regulated up- or downward in a time frame of 5 hours
List of references
1 | Vestas | Wind Energy and Ancillary Services | [9 empty] | http://www.anev.org/wp-content/uploads/2018/02/180216-Wind-Energy-Ancillary-Services-ANEV-Italy_Vestas.pdf
2 | Dotzauer et al. | How to measure flexibility – Performance indicators for demand driven power generation from biogas plants | [9 empty] | https://www.sciencedirect.com/science/article/pii/S0960148118312059#sec3
3 | ENTSO-E | MAF Data | [9 empty] | https://www.entsoe.eu/Documents/SDC%20documents/MAF/MAF_2018_Dataset.xlsx
4 | Agora | Flexibility in thermal power plants, with a focus on existing coal-fired power plants | [9 empty] | https://www.agora-energiewende.de/fileadmin2/Projekte/2017/Flexibility_in_thermal_plants/115_flexibility-report-WEB.pdf
5 | Danish Energy Agency | Flexibility in the Power System - Danish and European experiences | [9 empty] | https://ens.dk/sites/ens.dk/files/Globalcooperation/flexibility_in_the_power_system_v23-lri.pdf
6 | Deloitte | Assessing the economic conditions of Belgian pumped-hydroelectric storage: comparative review of profitability drivers in Europe and evaluation of the current situation | [9 empty] | https://www.creg.be/sites/default/files/assets/Consult/2018/1718/RA1718-Annex2.7.pdf
7 | e-Storage | Potential, Economic and Environmental Value of Large-Scale Energy Storage in Europe | [9 empty] | http://www.estorage-project.eu/wp-content/uploads/2013/06/eStorage-D3.2-Value-of-storage.pdf
8 | E-Cube Strategy Consultants | Market Response study 2017 – 2nd phase report | [9 empty] | https://www.elia.be/~/media/files/Elia/Products-and-services/Strategic-Reserve/Elia_Market%20Response_Implementation%20report.pdf
9 | Gils, H. | Assessment of the theoretical demand response potential in Europe | [9 empty] | https://ac.els-cdn.com/S0360544214001534/1-s2.0-S0360544214001534-main.pdf?_tid=d4fce1a0-6f34-465d-9c4f-523e95750e30&acdnat=1546943860_20cd8cd6d9355dd840de7e4fd94255bb
10 | Le Baut et al. | Characterization of flexibility resources and distribution networks | [9 empty] | http://smartnet-project.eu/wp-content/uploads/2017/05/D1.2_20170522_V1.1.pdf
11 | Brouwer et al. | Least-cost options for integrating intermittent renewables in low-carbon power systems | [9 empty] | https://ac.els-cdn.com/S0306261915012167/1-s2.0-S0306261915012167-main.pdf?_tid=52eeb980-f5b2-43f0-8d14-83cd9f435f58&acdnat=1546889876_5b2bf335e121403ca7dc9296eaf88b19
12 | IRENA | Green Hydrogen Cost Reduction | [9 empty] | https://www.irena.org/publications/2020/Dec/Green-hydrogen-cost-reduction
13 | Wartisla | Reciprocating engines as a source reciprocating engines as a source of flexibility in a power system | [9 empty] | https://www.cire.pl/pliki/2/2018/13___niewinski.pdf