## Contents
Adequacy and Flexibility study 2026-2036 - public consultation on the central scenario and data
This data is provided in the framework of the Adequacy and Flexibility study covering the years from 2026 to 2036. This study will be published before end of June 2025 as requested by law.
Data contained in this document is subject to a public consultation, starting 05/11/2024 and ending 05/12/2024 at 6:00 pm.
This Excel file contains the data related to the scenario framework of the study including economic and flexibility aspects. A text explaining the data and assumptions taken is also made available aswell as the explanatory note which is also submitted to this public consultation.
The methodology is fully available for the public consultation with detailed appendixes. The stakeholders can also use the presentation given during the Working Group Adequacy (05/11) as explanatory document where most of the data in this document are also presented.
Input data for market and flexibility simulations
1. Generation
1.1. Invidividually modelled thermal generation
1.2. Renewable energy sources and pofiled thermal units
2. Demand
2.1. Total electricity demand
2.2. Road transport demand
2.3. Building heat demand
2.4 Industrial demand
3. Flexibility
3.1. Storage
3.2. Industry flexibility
3.3. End-user flexibility
3.4. Electrolysers
4. Economic and technical variables
4.1. Fuel and CO2 prices
4.2. Investment costs
4.3. Outages
4.4. Flexibility characteristics
5. Flow-based domains
5.1. Main assumptions for flow-based domains
6. Other countries
6.1. Data for other countries

## 1.1. Ind. mod. thermal prod.
1.1. Individually modelled thermal generation
Sources | [9 empty] | Color Legend
- This information is based on official information known. | [9 empty] | Units that will not be part of the EVA unless are indicated by market parties to be at risk or that the support mechanism is to be stopped in the future
- Please inform us if any unit(s) are to be considered as not available for future time horizons or if any of those units are at risk of not being available and for which reasons. | [9 empty] | Units that are not available for the market or closed
Units will be part of the Economic Viability Assessment (EVA)
Available units and no EVA will be performed (nuclear)
Available units and no EVA will be performed (new CCGT)
Situation at end of the given year - considered as available for the EVA/market
Owner | Production unit name | Type | CHP | Fuel type | Net generation capacity [MW] | Efficiency [%] | VOM [€/MWh] | In-service year | Proposal to be considered in the Economic Viability Assessment (EVA) | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | Comments
Engie - Electrabel | TEREOS SYRAL GT | CCGT-GT | x | Gas | 43 | 45% | 2.4 | 1998 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | TEREOS SYRAL ST | CCGT-ST | x | Gas | 5 | 45% | 2.4 | 1998 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | AALTER TJ | TJ |  | Oil | 18 | 26% | 4 | 1967 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | AMERCOEUR 1 GT | CCGT-GT |  | Gas | 289 | 58% | 2.4 | 2009 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | AMERCOEUR 1 ST | CCGT-ST |  | Gas | 162 | 58% | 2.4 | 2009 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Luminus | ANGLEUR TG 31 | OCGT |  | Gas | 25 | 30% | 13.2 | 1978 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Luminus | ANGLEUR TG 32 | OCGT |  | Gas | 25 | 30% | 13.2 | 1978 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Luminus | ANGLEUR TG 41 | OCGT |  | Gas | 64 | 42% | 13.2 | 2012 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Luminus | ANGLEUR TG 42 | OCGT |  | Gas | 64 | 42% | 13.2 | 2012 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | AWIRS 4 | CL |  | Biomass | 75 | 38% | 3.6 | 1967 | - | no | no | no | no | no | no | no | no | no | no | no | no | no | Decommissioning: 01/09/2020 - https://economie.fgov.be/sites/default/files/Files/Energy/Mise-arret-definitive-unite-Awirs-4.pdf
Engie - Electrabel | BEERSE TJ | TJ |  | Oil | 32 | 26% | 4 | 1968 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Indaver | BEVEREN 2 INDAVER | IS |  | Waste | 21 | 36% | 3.6 | 1997 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Indaver | BEVEREN 3 INDAVER | IS |  | Waste | 24 | 36% | 3.6 | 2017 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
IneosPhenol | BEVEREN INEOS PHENOL CHEM | OCGT | x | Gas | 25.1 | 41% | 13.2 | 1994 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Indaver | BEVEREN SLECO | IS |  | Waste | 41 | 36% | 3.6 | 1997 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Biopower | BIOMASSA OOSTENDE | IS |  | Biomass | 18 | 36% | 3.6 | 2009 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Biostoom | BIOSTOOM OOSTENDE | IS |  | Waste | 19.4 | 36% | 3.6 | 2009 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Borealis | BOREALIS KALLO COGEN GT-ST | CCGT | x | Gas | 32 | 45% | 2.4 | 2024 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | Commissioning date expected - mid-2024 (01/07/2024 considered) https://www.spglobal.com/commodityinsights/en/market-insights/latest-news/petrochemicals/090122-pdh-project-in-belgium-delayed-to-mid-2024-as-borealis-retenders-construction-contracts
Engie - Electrabel | CIERREUX TJ | TJ |  | Oil | 18 | 26% | 4 | 2006 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | DOEL 1 | NU |  | Nuclear | 445 | 33% | 10.8 | 1975 | No | yes | no | no | no | no | no | no | no | no | no | no | no | no | Decommissioning: 15/02/2025 - https://economie.fgov.be/fr/themes/energie/sources-denergie/nucleaire/base-legale-de-la-sortie-du
Engie - Electrabel | DOEL 2 | NU |  | Nuclear | 445 | 33% | 10.8 | 1975 | No | yes | no | no | no | no | no | no | no | no | no | no | no | no | Decommissioning: 01/12/2025 - https://economie.fgov.be/fr/themes/energie/sources-denergie/nucleaire/base-legale-de-la-sortie-du
Engie - Electrabel | DOEL 3 | NU |  | Nuclear | 1006 | 33% | 10.8 | 1982 | No | no | no | no | no | no | no | no | no | no | no | no | no | no | Decommissioning: 01/10/2022 - https://economie.fgov.be/fr/themes/energie/sources-denergie/nucleaire/base-legale-de-la-sortie-du
Engie - Electrabel | DOEL 4 | NU |  | Nuclear | 1026 | 33% | 10.8 | 1985 | No | yes | yes* | yes* | yes* | yes | yes | yes | yes | yes | yes | yes | no | no | Lifetime extension - Considered operational from winter 2025-26 with only availability during winter until summer 2028 included (*). Updated installed capacity - based on information published on Nordpool - https://umm.nordpoolgroup.com/#/messages?publicationDate=all&eventDate=all&units=22WDOELX40000793&units=22WTIHANG000242R Decommissioning: 31/10/2035
Engie - Electrabel | DROGENBOS GT1 | CCGT-GT |  | Gas | 150 | 52% | 2.4 | 1994 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | DROGENBOS GT2 | CCGT-GT |  | Gas | 150 | 52% | 2.4 | 1994 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | DROGENBOS ST | CCGT-ST |  | Gas | 160 | 52% | 2.4 | 1994 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Luminus | EDF LUMINUS SERAING NEW | CCGT |  | Gas | 885 | 61% | 2.4 | 2025 | No | no | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | Contracted in the CRM Y-4 auction for Delivery Period 2025-26 for a duration of 15 years - https://www.elia.be/en/grid-data/adequacy/crm-auction-results
Luminus | EDF LUMINUS SERAING ST | CCGT-ST |  | Gas | 170 | 52% | 2.4 | 1994 | Yes | no | no | no | no | no | no | no | no | no | no | no | no | no | Art. 4bis - Decommissioning date: 18/04/2024 - https://economie.fgov.be/sites/default/files/Files/Energy/tijdelijke-buitenwerkingstelling-stoomturbinesteg-centrale-seraing.pdf
Luminus | EDF LUMINUS SERAING TG1 | CCGT-GT |  | Gas | 150 | 34.4% | 13.2 | 1994 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Luminus | EDF LUMINUS SERAING TG2 | CCGT-GT |  | Gas | 150 | 34.4% | 13.2 | 1994 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Euro-silo | EURO-SILO | CCGT | x | Gas | 12.9 | 45% | 2.4 | 2013 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Indaver | E-WOOD | IS |  | Waste | 22 | 36% | 3.6 | 2022 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | E-wood production unit came in operation in December 2022.
Engie - Electrabel | FLÉMALLE NEW | CCGT |  | Gas | 890 | 61% | 2.4 | 2025 | No | no | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | Contracted in the CRM Y-4 auction for Delivery Period 2025-26 for a duration of 15 years - https://www.elia.be/en/grid-data/adequacy/crm-auction-results
Engie - Electrabel | FLUXYS ZEEBRUGGE | OCGT | x | Gas | 40 | 41% | 13.2 | 1996 | No | yes | no | no | no | no | no | no | no | no | no | no | no | no | Art 4. bis - Decommissioning: 01/04/2025 - https://economie.fgov.be/fr/themes/energie/securite-dapprovisionnement/electricite/mecanismes-de-capacite/reserve-strategique/notifications-de-mise-larret
Green Power | GREENPOWER OOSTENDE | IS | x | Waste | 20 | 36% | 3.6 | 2010 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Luminus | HAM 31 | OCGT |  | Gas | 58 | 42% | 13.2 | 2008 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Luminus | HAM 32 | OCGT |  | Gas | 58 | 42% | 13.2 | 2008 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Luminus | HAM GENT-GT | CCGT | x | Gas | 39 | 45% | 13.2 | 1997 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | HERDERSBRUG GT1 | CCGT-GT |  | Gas | 157 | 51% | 2.4 | 1998 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | HERDERSBRUG GT2 | CCGT-GT |  | Gas | 156.3 | 51% | 2.4 | 1998 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | HERDERSBRUG ST | CCGT-ST |  | Gas | 167 | 51% | 2.4 | 1998 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
INEOS | INESCO GT1 | CCGT-GT | x | Gas | 44.8 | 58% | 2.4 | 2006 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
INEOS | INESCO GT2 | CCGT-GT | x | Gas | 44.8 | 58% | 2.4 | 2006 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
INEOS | INESCO ST | CCGT-ST | x | Gas | 48.5 | 58% | 2.4 | 2006 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
INTRADEL | INTRADEL | IS |  | Waste | 32 | 36% | 3.6 | 2008 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
IPALLE | IPALLE THUMAIDE | IS |  | Waste | 34 | 36% | 3.6 | 1986 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | ISVAG | IS |  | Waste | 12 | 36% | 3.6 | 1989 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Lampiris | IVBO | IS |  | Waste | 16 | 36% | 3.6 | 2012 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Luminus | IZEGEM | CCGT | x | Gas | 20 | 45% | 2.4 | 2015 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Inovyn | JEMEPPE-SUR-SAMBRE GT1 | CCGT-GT | x | Gas | 48 | 45% | 2.4 | 2000 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Inovyn | JEMEPPE-SUR-SAMBRE GT2 | CCGT-GT | x | Gas | 48 | 45% | 2.4 | 2000 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Inovyn | JEMEPPE-SUR-SAMBRE ST | CCGT-ST | x | Gas | 10 | 45% | 2.4 | 2000 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | KNIPPEGROEN STEG | CL |  | Gas | 305 | 42% | 3.6 | 2010 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Lillo Energy | LILLO DEGUSSA GT1 | CCGT-GT | x | Gas | 43 | 45% | 2.4 | 1999 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Lillo Energy | LILLO DEGUSSA GT2 | CCGT-GT | x | Gas | 32 | 45% | 2.4 | 2009 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Lillo Energy | LILLO DEGUSSA ST | CCGT-ST | x | Gas | 10 | 45% | 2.4 | 2009 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Direct Energie | MARCINELLE ENERGIE TGV | CCGT |  | Gas | 413 | 52% | 2.4 | 2011 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | MONSANTO LILLO WKK EBL | OCGT | x | Gas | 43 | 41% | 13.2 | 2000 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | NOORDSCHOTE TJ | TJ |  | Oil | 18 | 26% | 4 | 1971 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | OORDEREN BAYER | OCGT | x | Gas | 43 | 41% | 13.2 | 2000 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Luminus | RINGVAART STEG | CCGT |  | Gas | 385 | 55% | 2.4 | 1997 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | RODENHUIZE 4 | CL |  | Biomass | 205 | 38% | 3.6 | 2009 | No | no* | no* | no* | no* | no* | no* | no* | no* | no* | no* | no* | no* | no* | As of 24.02.23 Rodenhuize 4 will be used as a backup unit to Zelzate Knippegroen for burning steel gas when Knippegroen is unavailable - https://umm.nordpoolgroup.com/#/messages/73aa666e-c3ff-4224-a1e5-6ad751abf122/1 In addition, the unit is considered to be able to run at Pmin (65 MW) simultaneously with Knippegroen in case of scarcity situation (*).
Engie - Electrabel | SAINT-GHISLAIN STEG | CCGT |  | Gas | 385 | 51% | 2.4 | 2000 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | Capacity increases from 378 MW to 385 MW based on NordPool - https://umm.nordpoolgroup.com/#/messages?publicationDate=all&eventDate=custom&areas=10YBE----------2&units=22WSAINT-000221B&status=active&eventDateStart=1970-01-01&eventDateStop=2124-09-02
Engie - Electrabel | SAPPI LANAKEN GT | OCGT | x | Gas | 43 | 41% | 13.2 | 1997 | No | no | no | no | no | no | no | no | no | no | no | no | no | no | Art 4. bis - Decommissioning: 20/02/2024 - https://economie.fgov.be/fr/themes/energie/securite-dapprovisionnement/electricite/mecanismes-de-capacite/reserve-strategique/notifications-de-mise-larret
Centre de Tri | SCHAERBEEK SIOMAB 1 | IS |  | Waste | 15 | 36% | 3.6 | 1985 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Centre de Tri | SCHAERBEEK SIOMAB 2 | IS |  | Waste | 15 | 36% | 3.6 | 1985 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Centre de Tri | SCHAERBEEK SIOMAB 3 | IS |  | Waste | 15 | 36% | 3.6 | 1985 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
EXXONMOBIL | SCHELDELAAN EXXONMOBIL | CCGT | x | Gas | 140 | 45% | 2.4 | 2008 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
STORA | STORA LANGERBRUGGE CHP 1 | CL | x | Biomass | 10 | 38% | 3.6 | 2006 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
STORA | STORA LANGERBRUGGE CHP 2 | CL | x | Biomass | 40 | 38% | 3.6 | 2010 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
TAMINCO | TAMINCO GENT CHP | OCGT | x | Gas | 6.3 | 41% | 13.2 | 2009 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | TIHANGE 1N | NU |  | Nuclear | 481 | 33% | 10.8 | 1975 | No | yes | no | no | no | no | no | no | no | no | no | no | no | no | Decommissioning: 01/10/2025 - https://economie.fgov.be/fr/themes/energie/sources-denergie/nucleaire/base-legale-de-la-sortie-du
Engie - Electrabel | TIHANGE 1S | NU |  | Nuclear | 481 | 33% | 10.8 | 1975 | No | yes | no | no | no | no | no | no | no | no | no | no | no | no | Decommissioning: 01/10/2025 - https://economie.fgov.be/fr/themes/energie/sources-denergie/nucleaire/base-legale-de-la-sortie-du
Engie - Electrabel | TIHANGE 2 | NU |  | Nuclear | 1008 | 33% | 10.8 | 1983 | No | no | no | no | no | no | no | no | no | no | no | no | no | no | Decommissioning: 01/02/2023 - https://economie.fgov.be/fr/themes/energie/sources-denergie/nucleaire/base-legale-de-la-sortie-du
Engie - Electrabel | TIHANGE 3 | NU |  | Nuclear | 1030 | 33% | 10.8 | 1985 | No | yes | yes* | yes* | yes* | yes | yes | yes | yes | yes | yes | yes | no | no | Lifetime extension - Considered operational from winter 2025-26 with only availability during winter until summer 2028 included (*). Updated installed capacity - based on information published on Nordpool - https://umm.nordpoolgroup.com/#/messages?publicationDate=all&eventDate=all&units=22WDOELX40000793&units=22WTIHANG000242R Decommissioning: 31/10/2035
T-Power | T-POWER | CCGT |  | Gas | 425 | 58% | 2.4 | 2011 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | TURBOJET VOLTA | TJ |  | Oil | 18 | 26% | 4 | 1971 | Yes | no | no | no | no | no | no | no | no | no | no | no | no | no | Art. 4bis - Decommissioning date: 26/08/2023 - https://economie.fgov.be/sites/default/files/Files/Energy/22-54-EBL-FOD-N-Mahieu-fermeture-TJ-VOLTA-Art4-%20GHS-signed.pdf
Engie - Electrabel | VILVOORDE GT | CCGT-GT |  | Gas | 255 | 37% | 13.2 | 2001 | No | no | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | Available as from the 1st of November 2025 - https://umm.nordpoolgroup.com/#/messages/937ab00f-4cd1-4aca-9c2d-0ef05594fd28/2 Efficiency as OCGT https://flux50.com/media/2962/Rudi%20Hermans%2020190117.pdf
Engie - Electrabel | VILVOORDE ST | CCGT-ST |  | Gas | 105 | 55% | 2.4 | 2001 | No | no | no | no | no | no | no | no | no | no | no | no | no | no | Based on information published on REMIT, decommissioning 01/04/2023
TOTAL | WILMARSDONK TOTAL GT1 | OCGT | x | Gas | 43 | 41% | 13.2 | 2000 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
TOTAL | WILMARSDONK TOTAL GT2 | OCGT | x | Gas | 43 | 41% | 13.2 | 2000 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
TOTAL | WILMARSDONK TOTAL GT3 | OCGT | x | Gas | 43 | 41% | 13.2 | 2000 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Zandvliet Power NV | ZANDVLIET POWER | CCGT | x | Gas | 419 | 57% | 2.4 | 2024 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | Repowering to 419 MW as of November 2024
Engie - Electrabel | ZEDELGEM TJ | TJ |  | Oil | 18 | 26% | 4 | 1968 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | ZEEBRUGGE TJ | TJ |  | Oil | 18 | 26% | 4 | 1968 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | ZELZATE TJ | TJ |  | Oil | 18 | 26% | 4 | 2003 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | ZWIJNDRECHT LANXESS GT | CCGT-GT | x | Gas | 43 | 45% | 13.2 | 2009 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | ZWIJNDRECHT LANXESS ST | CCGT-ST | x | Gas | 15 | 45% | 2.4 | 2009 | No | no | no | no | no | no | no | no | no | no | no | no | no | no | Art 4. bis - Decommissioning: 01/09/2023 - https://economie.fgov.be/fr/themes/energie/securite-dapprovisionnement/electricite/mecanismes-de-capacite/reserve-strategique/notifications-de-mise-larret
Legend Unit-Type
CCGT | Combined Cycle
CCGT-GT | Combined Cycle - Gas Turbine
CCGT-ST | Combined Cycle - Steam Turbine
CL | Classic
GT | Gas Turbine
ST | Steam Turbine
IS | Incineration Station
NU | Nuclear
TJ | TurboJet
CHP | Cogeneration Unit

## 1.2. Renewable & profiled
1.2. Evolution of renewable energy sources and profiled thermal units
Generation capacity at the end of the mentioned year [MW]
Generation type |  | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
| Wind | 5674 | 6108 | 6542 | 6976 | 7410 | 7844 | 8978 | 12092 | 12405 | 12719 | 13033 | 13346 | 13660
| Wind onshore | 3413 | 3847 | 4281 | 4715 | 5149 | 5583 | 6017 | 6331 | 6644 | 6958 | 7272 | 7585 | 7899
| Wind offshore | 2261 | 2261 | 2261 | 2261 | 2261 | 2261 | 2961 | 5761 | 5761 | 5761 | 5761 | 5761 | 5761
| Photovoltaics | 11181 | 12072 | 12962 | 13854 | 14744 | 15635 | 16525 | 17415 | 18306 | 19196 | 20088 | 20978 | 21869
| Hydro RoR | 135.7143 | 141.4286 | 147.1429 | 152.8571 | 158.5714 | 164.2857 | 170 | 170 | 170 | 170 | 170 | 170 | 170
| Gas CHP - profiled | 1435 | 1494 | 1519 | 1531 | 1544 | 1554 | 1567 | 1567 | 1567 | 1567 | 1567 | 1567 | 1567
| Biomass - profiled | 521 | 521 | 536 | 543 | 550 | 557 | 564 | 564 | 564 | 564 | 564 | 564 | 564
| Waste - profiled | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
See below for more information on the assumptions behind the projection of each category.
| Solar PV | [13 empty] | [MWp] Capacity assumed at the end of the mentioned year
[16 empty] | [MWp] | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
[15 empty] | Historic (IEA) | Belgium | 1007 | 1979 | 2647 | 2902 | 3014 | 3131 | 3330 | 3620 | 4000 | 4640 | 5570 | 6580 | 7468
[15 empty] | AdeqFlex'23 | Belgium | [13 empty] | 8330 | 9210 | 10090 | 10970 | 11850 | 12730 | 13610 | 14490 | 15370 | 16250 | 17130 | 18010
[15 empty] | AdeqFlex'25 | Belgium | [13 empty] | 9701 | 11181 | 12072 | 12962 | 13854 | 14744 | 15635 | 16525 | 17415 | 18306 | 19196 | 20088 | 20978 | 21869
[15 empty] | AdeqFlex'25 | Flanders | [13 empty] | 6987 | 8074 | 8595 | 9116 | 9637 | 10158 | 10679 | 11200 | 11721 | 12242 | 12763 | 13284 | 13805 | 14326
[15 empty] | AdeqFlex'25 | Wallonia | [13 empty] | 2429 | 2807 | 3173 | 3538 | 3904 | 4269 | 4635 | 5000 | 5365 | 5731 | 6096 | 6462 | 6827 | 7193
[15 empty] | AdeqFlex'25 | Brussels | [13 empty] | 285 | 300 | 304 | 308 | 313 | 317 | 321 | 325 | 329 | 333 | 337 | 342 | 346 | 350
Best estimate for 2024 based on extrapolated data
Solar photovoltaic (PV) energy is becoming an increasingly significant part of Belgium's electricity landscape. Belgium has seen substantial growth in solar PV installations over recent years. The 2023 year was a record year with nearly 2,000 MWp installed. The total installed capacity in Belgium has now reached more than 10 GWp. Even though the high increase observed in 2023 has been influenced by the recent energy crisis and by the rush in Wallonia to benefit of the advantages of net metering, the installed capacity is expected to continue growing in Belgium (reduced solar panel prices, legislation in Flanders for certain consumer to be equipped with solar pannels, etc.). Note that the data in the Excel file and in this document are expressed in [MWp] or [GWp] – also called MWpeak / MWcrete (on the DC side of the solar pannel). The proposed evolution of solar capacity in Belgium is based on the following assumptions: - A best estimate for installed capacity end of 2024 (using online data from BRUGEL for Brussels, data from SPWallonia and online data from VEKA for Flanders ); - Interpolation between 2024 best estimate and 2030, considering for 2030 the latest official targets o For Wallonia, a target of 5 GWp is assumed, considering the 5100 GWh stated in the updated draft NECP; o For Brussels, a target of 0.325 GWp is assumed, considering the 334 GWh stated in the updat-ed draft NECP; o For Flanders, a target of 11.2 GWp is assumed, considering the recent 10 GW announced in the recent Flemish governmental agreement (target assumed to be in GWac and considering conversion factor MWp/MWac of 1.12). - Extrapolation based on 2025-2030 growth rate for the period after 2030. This leads to a proposed installation rate of 900 MWp per year in Belgium with a total capacity of 16.5 GW by 2030.
| Onshore Wind | [13 empty] | [MW] Capacity assumed at the end of the mentioned year
[16 empty] | [MW] | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
[15 empty] | Historic (IEA) | Belgium | 716 | 873 | 989 | 1072 | 1236 | 1464 | 1658 | 1915 | 2130 | 2320 | 2471 | 2726 | 3058
[15 empty] | AdeqFlex'23 | Belgium | [13 empty] | 3268 | 3598 | 3928 | 4258 | 4588 | 4918 | 5248 | 5578 | 5908 | 6238 | 6568 | 6898
[15 empty] | AdeqFlex'25 | Belgium | [13 empty] | 3260 | 3413 | 3847 | 4281 | 4715 | 5149 | 5583 | 6017 | 6331 | 6644 | 6958 | 7272 | 7585 | 7899
[15 empty] | AdeqFlex'25 | Flanders | [13 empty] | 1827 | 1880 | 2033 | 2187 | 2340 | 2493 | 2647 | 2800 | 2833 | 2866 | 2899 | 2932 | 2965 | 2998
[15 empty] | AdeqFlex'25 | Wallonia | [13 empty] | 1433 | 1533 | 1814 | 2094 | 2375 | 2656 | 2936 | 3217 | 3498 | 3778 | 4059 | 4340 | 4620 | 4901
[15 empty] | AdeqFlex'25 | Brussels
Best estimate for 2024 based on extrapolated data
Regarding onshore wind, the recent Flemish governmental agreement (Sep. 2024) has increased the 2030 target from 2.6 GW to 2.8 GW. In Wallonia, the Walloon governmental agreement confirmed its commitment to achieve the European objectives while revising the wind onshore development framework. The proposed evolution of onshore wind capacity in Belgium for the CENTRAL scenario is based on the following assumptions: - A best estimate for installed capacity end of 2024 about 3.4 GW (using EDORA data for Wallonia and VEKA data for Flanders) - Interpolation between 2024 best estimate and 2030, considering for 2030 the latest official targets o For Wallonia, a target of 3.2 GW is assumed, considering the 6200 GWh stated in the updated draft NECP; o For Flanders, a target of 2.8 GW is assumed, considering the announcement in the recent Flemish governmental agreement. - Extrapolation based on 2025-2030 growth rate for the period after 2030 for Wallonia. For Flanders, a slower uptake after 2030 is considered (limited additional capacity under current permitting condi-tions, according to exchanges with the Region).
| Offshore Wind | [13 empty] | [MW] Capacity assumed at the end of the mentioned year
[16 empty] | [MW] | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
[15 empty] | Historic | Belgium | 200 | 200 | 400 | 400 | 700 | 700 | 700 | 900 | 1100 | 1570 | 2261 | 2261 | 2261
[15 empty] | AdeqFlex'23 | Belgium | [13 empty] | 2261 | 2261 | 2261 | 2261 | 2261 | 2261 | 2961 | 5760 | 5760 | 5760 | 5760 | 5760
[15 empty] | AdeqFlex'25 | Belgium | [13 empty] | 2261 | 2261 | 2261 | 2261 | 2261 | 2261 | 2261 | 2961 | 5761 | 5761 | 5761 | 5761 | 5761 | 5761
When it comes to offshore wind, Belgium already accounts for 2,261 MW of installed capacity. Additional ca-pacity related to the Princess Elisabeth Island (PEI) project is considered in the proposed trajectory, based on the foreseen realisation timing of the validated Federal Development Plan. - The first phase of PEI, with an additional 700 MW, is to be realised by end of 2029 and is proposed to be assumed as available for adequacy as from winter 2030/31 in this study. - The second phase of PEI, with an additional 2,800 MW, is to be realised by end of 2030 and is proposed to be assumed as available for adequacy as from winter 2031/32 in this study.
| Run-of-river hydroelectricity | [13 empty] | [MW] Capacity assumed at the end of the mentioned year
[16 empty] | [MW] | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
[15 empty] | Historic (Renouvelle) | Belgium | 111.56 | 110.31 | 109.94 | 112.24 | 114.4 | 105.9 | 106.88 | 109.43 | 107.7 | 106.55 | 116.47 | 120.82 | 124.14
[15 empty] | AdeqFlex'23 | Belgium | [13 empty] | 129 | 133 | 137 | 140 | 143 | 145 | 148 | 151 | 154 | 157 | 160 | 163
[15 empty] | AdeqFlex'25 | Belgium | [13 empty] | 130 | 135.7143 | 141.4286 | 147.1429 | 152.8571 | 158.5714 | 164.2857 | 170 | 170 | 170 | 170 | 170 | 170 | 170
The existing run-of-river hydroelectricity capacity in Belgium consist of small hydro units installed along the river. Most of the capacity is located in Wallonia, along the Meuse. According to the Bilan Energétique de Wal-lonie 2020, the evolution of the installed capacity in Wallonia seemed to stagnate since the 1980’s . The proposed trajectory for run-of-river hydroelectricity is based on the following assumptions: In the NECP, a target of 440 GWh of run-of-river hydroelectricity towards 2030 is specified. Based on - Best estimate for installed capacity end of 2024 about 136 MW based data from estimation from PISA database and historical data; - Interpolation between 2024 best estimate and 2030, considering a target of 170 MW for Belgium (based on the 440 GWh specified for Wallonia in NECP and historical capacity factors), a capacity which is then maintained constant.
| Decentralised Biomass, Waste, CHP | [13 empty] | [MW] Capacity assumed at the end of the mentioned year
[16 empty] | [MW] | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
[15 empty] | AdeqFlex'25 | Waste | [13 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
[15 empty] | AdeqFlex'25 | Biomass | [13 empty] | 518 | 521 | 521 | 536 | 543 | 550 | 557 | 564 | 564 | 564 | 564 | 564 | 564 | 564
In this category, profiled thermal units are considered. Those are usually smaller decentralised production units, usually connected to the distribution grid (DSO). A database covering those projects is maintained by Elia and updated on monthly basis by exchanges with DSO and grid users. This also includes new projects that are being developped. Biomass & waste: Regarding decentralised biomass and waste units (modelled as profiled thermal units in the simulations), the existing capacity is considered constant (no closure assumed) and about 40 MW of new projects in biomass by 2030 are assumed, based on information available in the PISA database. CHP: The existing capacity is is based on existing and future projects. To do so, Elia uses the PISA database: an Elia database containing all units of the Belgian system (which are connected to the TSO and DSO grids), which is based on data that DSOs communicate to Elia on a regular basis. In addition to the known future projects, a rather optimistic assumption is taken by considering no potential additional decommissioning of the existing capacities, considering that those units can still participate in CRM auctions, at least until the mechanism is available. | [14 empty] | AdeqFlex'25 | CHP | [13 empty] | 1417 | 1435 | 1494 | 1519 | 1531 | 1544 | 1554 | 1567 | 1567 | 1567 | 1567 | 1567 | 1567 | 1567

## 2.1. Tot. elec. demand
2.1. Total electricity consumption
The total electricity demand for Belgium is constructed with several building blocks.
It It notably builts on the tool developped by Climact and used in the previous editions of the Adequacy & Flexibility study (2021, 2023), where the methodology used is described in the following report:
https://www.elia.be/-/media/project/elia/elia-site/public-consultations/2020/20200603_total-electricity-demand-forecasting_en.pdf
The different building blocks included in the projection of total electricity demand are the following:
1) Existing usages: electricity demand of today and how it will evolves. Drivers of its evolution are described in the word document.
2) It includes the trends in terms of electrification of transport & heating
cfr. Section 2.2 & 2.3
3) it includes an update of the load management: a bottom-up exercise carried out with TSO-connected customers to estimate future consumption from the industry and new large-scale loads. Due to uncertainty, this part shows a range of values.
The load management has been presented to stakeholders in WG Adequacy on 27/08/2024
cfr. Section 2.4
These build the proposed load projection for the CENTRAL scenario. A low and high trajectory are also proposed. These covers respectively for the low and high projection:
1) Aligned Low and High scenario from the Load Management (which covers new large-scale loads)
2) Either a partial or full demand recovery (estimated by E-CUBE in the PRICED study)
3) for the low trajectory solely, potential closures of industry as at risk (identified by E-CUBE in the PRICED study)
Status
| Year | [6 empty] | New large scale loads |  | Demand destruction - Industry at risk | Recovery - residential & tertiary |  | Losses | AdeqFlex'25 public consultation load proposal |  |  |  |  | Range for load scenario
TWh |  | Historical normalised total demand | Existing usages | Additional EV | Additional HP | Existing usages + EV + HP | LOW | BEST ESTIMATE | HIGH | LOW | Partial | Total |  | LOW | BEST ESTIMATE | HIGH | Historical | Total Demand incl. EV & HP | Min Range | Max Range | AdeqFlex'25 public consultation load proposal | Min Range increase | Max Range increase
historical | 2010 | 89.3 |  |  |  | 89.3 | [10 empty] | 89.3
historical | 2011 | 88.2 |  |  |  | 88.2 | [10 empty] | 88.2
historical | 2012 | 84.7 |  |  |  | 84.7 | [10 empty] | 84.7
historical | 2013 | 85.8 |  |  |  | 85.8 | [10 empty] | 85.8
historical | 2014 | 89.4 |  |  |  | 89.4 | [10 empty] | 89.4
historical | 2015 | 88.3 |  |  |  | 88.3 | [10 empty] | 88.3
historical | 2016 | 86.4 |  |  |  | 86.4 | [10 empty] | 86.4
historical | 2017 | 87.4 |  |  |  | 87.4 | [10 empty] | 87.4
historical | 2018 | 88 |  |  |  | 88 | [10 empty] | 88
historical | 2019 | 85.7 |  |  |  | 85.7 | [10 empty] | 85.7
historical | 2020 | 82.1 |  |  |  | 82.1 | [10 empty] | 82.1
historical | 2021 | 84.7 |  |  |  | 84.7 | [10 empty] | 84.7
historical | 2022 | 82.9 |  |  |  | 82.9 | [10 empty] | 82.9
historical | 2023 | 80.1 |  |  |  | 80.1 | [10 empty] | 80.1
best estimate | 2024 | 81.8 |  |  |  | 81.8 | [7 empty] | 81.8 | 81.8 | 81.8 | 81.8 |  |  |  | 81.8
| 2025 |  | 82.09 | 0.97 | 0.18 | 83.24 | 0.88 | 1.52 | 2.52 | -0.5 | 0.01 | 0.02 | 0.11 | 83.74 | 84.88 | 85.89 |  | 83.24 | 83.74 | 85.89 | 84.88 | 83.74 | 2.15
| 2026 |  | 82.3 | 2.11 | 0.37 | 84.78 | 1.85 | 2.78 | 4.39 | -0.5 | 0.06 | 0.08 | 0.25 | 86.44 | 87.87 | 89.5 |  | 84.78 | 86.44 | 89.5 | 87.87 | 86.44 | 3.06
| 2027 |  | 82.51 | 3.46 | 0.59 | 86.56 | 2.67 | 4.61 | 6.99 | -0.5 | 0.29 | 0.41 | 0.36 | 89.38 | 91.82 | 94.32 |  | 86.56 | 89.38 | 94.32 | 91.82 | 89.38 | 4.94
| 2028 |  | 82.7 | 4.82 | 0.82 | 88.34 | 3.34 | 6.67 | 12 | -0.5 | 0.45 | 0.63 | 0.46 | 92.09 | 95.92 | 101.43 |  | 88.34 | 92.09 | 101.43 | 95.92 | 92.09 | 9.34
| 2029 |  | 82.92 | 6.35 | 1.06 | 90.33 | 5.02 | 9.39 | 15.7 | -0.5 | 0.45 | 0.63 | 0.56 | 95.86 | 100.73 | 107.22 |  | 90.33 | 95.86 | 107.22 | 100.73 | 95.86 | 11.36
| 2030 |  | 83.13 | 7.81 | 1.34 | 92.28 | 6.44 | 13.64 | 20.07 | -0.5 | 0.45 | 0.63 | 1 | 99.67 | 107.37 | 113.98 |  | 92.28 | 99.67 | 113.98 | 107.37 | 99.67 | 14.31
| 2031 |  | 83.33 | 8.94 | 1.62 | 93.89 | 8.08 | 15.57 | 22.98 | -0.5 | 0.45 | 0.63 | 1.24 | 103.16 | 111.15 | 118.74 |  | 93.89 | 103.16 | 118.74 | 111.15 | 103.16 | 15.58
| 2032 |  | 83.53 | 10.09 | 1.93 | 95.55 | 11.5 | 18.1 | 30.02 | -0.5 | 0.45 | 0.63 | 1.48 | 108.48 | 115.58 | 127.68 |  | 95.55 | 108.48 | 127.68 | 115.58 | 108.48 | 19.2
| 2033 |  | 83.73 | 11.28 | 2.24 | 97.26 | 13.06 | 21.79 | 33.42 | -0.5 | 0.45 | 0.63 | 1.71 | 111.98 | 121.21 | 133.02 |  | 97.26 | 111.98 | 133.02 | 121.21 | 111.98 | 21.04
| 2034 |  | 83.93 | 12.48 | 2.58 | 98.99 | 14.38 | 23.88 | 34.54 | -0.5 | 0.45 | 0.63 | 1.95 | 115.27 | 125.27 | 136.11 |  | 98.99 | 115.27 | 136.11 | 125.27 | 115.27 | 20.84
| 2035 |  | 84.13 | 13.61 | 2.93 | 100.67 | 15.6 | 25.89 | 35.55 | -0.5 | 0.45 | 0.63 | 2.19 | 118.41 | 129.2 | 139.04 |  | 100.67 | 118.41 | 139.04 | 129.2 | 118.41 | 20.63
| 2036 |  | 84.33 | 14.93 | 3.3 | 102.56 | 17.12 | 28.22 | 36.87 | -0.5 | 0.45 | 0.63 | 2.42 | 122.05 | 133.65 | 142.48 |  | 102.56 | 122.05 | 142.48 | 133.65 | 122.05 | 20.43
0
Best estimate for 2024 [TWh]

## 2.2. Road transport demand
2.2 Electrification of the transport sector
Passenger cars
Key Drivers
Yearly passenger car sales assumed to continue the trend of 2019-2023
All regions reach 100% BEV car sales by 2035 due to EU regulation
Company cars: 100% BEV sales in all regions by 2029 due to federal fiscal measures
Sources used
BE - stock | https://public.flourish.studio/story/2341586/
BE - sales | 2.B.4. Evolution des immatriculations de voitures neuves par type de propriétaire et par région.xls (live.com)
EU | (Fit for 55: MEPs back objective of zero emissions for cars and vans in 2035 ¦ News ¦ European Parliament (europa.eu)
BE | Minister Van Peteghem maakt van bedrijfswagens en laadpalen de hefbomen naar een groener wagenpark ¦ Vincent Van Peteghem (belgium.be)
| Unit | Value
Sales - company | thousand units/y | 260
Sales - private | thousand units/y | 180
Stock at end of year [Thousands]
Passenger car stock [Thousands] | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
passenger car - company - BEV | 35 | 66 | 147 | 244 | 384 | 571 | 777 | 964 | 1154 | 1312 | 1376 | 1436 | 1494 | 1536 | 1552 | 1563
passenger car - company - PHEV | 109 | 153 | 225 | 278 | 328 | 333 | 310 | 275 | 226 | 177 | 129 | 80 | 34 | 4 | 0 | 0
passenger car - private - BEV | 15 | 22 | 34 | 45 | 62 | 90 | 130 | 184 | 265 | 367 | 487 | 623 | 783 | 953 | 1130 | 1306
passenger car - private - PHEV | 10 | 25 | 53 | 62 | 85 | 106 | 118 | 129 | 134 | 136 | 135 | 134 | 133 | 131 | 127 | 123
Total | 169 | 266 | 459 | 629 | 859 | 1100 | 1335 | 1552 | 1779 | 1992 | 2127 | 2273 | 2444 | 2624 | 2809 | 2992
Share of total stock | 2.9% | 4.5% | 7.8% | 10.6% | 14.5% | 18.6% | 22.5% | 26.2% | 30% | 33.7% | 35.9% | 38.5% | 41.3% | 44.4% | 47.5% | 50.6%
Consumption parameters | Unit | Value
Usage - company | km/year | 22750.4363
Usage - private | km/year | 12350
Consumption - BEV | kWh/100km | 19
Consumption - PHEV company | kWh/100km | 3
Consumption - PHEV private | kWh/100km | 9.5
LDV Freight (Vans)
Key Drivers
Yearly vans sales assumed to continue the trend of 2018-2022
Electrification of Vans follows the passenger car segment, but with a delayed uptake.
European regulation also applicable for vans from 2035, sucht that 100% BEV sales are reached in 2035 (2)
Flanders: alligned with Fluvius assumptions
Sources used
BE - vans stock | TOTAL: 2.C.8. Parc des VU par marque.xls (live.com)
EU | (2) Fit for 55: MEPs back objective of zero emissions for cars and vans in 2035 ¦ News ¦ European Parliament (europa.eu)
| Unit | Value
Sales - vans | thousand units/y | 72
Stock at end of year [Thousands]
Vans stock [Thousands] | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
vans - BEV | 2.5 | 4.3 | 7.4 | 14.5 | 40 | 75 | 125 | 178 | 233 | 286 | 337 | 386 | 432 | 477 | 527 | 580
vans - PHEV | 0 | 0 | 0.2 | 1.1 | 2 | 2.8 | 3.7 | 4.4 | 5.2 | 4.9 | 4.7 | 4.4 | 4.2 | 3.9 | 3.7 | 3.5
Total | 2.5 | 4.3 | 7.6 | 15.6 | 42 | 77.8 | 128.7 | 182.4 | 238.2 | 290.9 | 341.7 | 390.4 | 436.2 | 480.9 | 530.7 | 583.5
Share of total stock | 0.3% | 0.5% | 0.8% | 1.7% | 4.4% | 8% | 12.9% | 17.9% | 22.7% | 27.1% | 31.1% | 34.8% | 38.1% | 41.3% | 45.2% | 49.3%
| Unit | Value
Usage | km/year | 16800
Efficiency - BEV | kWh/100km | 30
Efficiency - PHEV | kWh/100km | 15
HDV freight (Trucks)
Key Drivers
Yearly trucks sales assumed to continue the trend of 2018-2022
Electrification driven by EU regulation: 40% BEV sales by 2030, 60% by 2035
Flanders: alligned with Fluvius assumptions
Sources used
BE - stock | 2.C.1. Parc des véhicules au 31 décembre de l&#39;année correspondante.xls (live.com)
EU | Agreement on strong EU targets to reduce CO2 emissions (europa.eu)
| Unit | Value
Sales - trucks | thousand units/y | 9.3
Stock at end of year [Thousands]
Trucks stock [Thousands] | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
Trucks - BEV | 0 | 0 | 0 | 0.1 | 0.3 | 0.6 | 1.5 | 3.2 | 6.4 | 10.1 | 14.1 | 18.3 | 23 | 28 | 33 | 41
Share of total stock [%] | 0% | 0% | 0% | 0.1% | 0.2% | 0.4% | 1% | 2.1% | 4.2% | 6.7% | 9.3% | 12% | 14.7% | 17.9% | 21.2% | 26.2%
| Unit | Value
Usage (km/year) | km/year | 58700
Efficiency (kWh/100km) | kWh/100km | 120
Buses
Key Drivers
Pledges & ambitions by public bus companies are the key driver for this segment
EU: urban buses to be zero-emission as from 2035
FL: De Lijn to reach 100% BEV by 2035 - alligned with Fluvius
BXL: MIVB to reach 100% BEV by 2035
TEC: towars 100% BEV, but no clear target date
Sources used
BE -stock | 2.C.1. Parc des véhicules au 31 décembre de l&#39;année correspondante.xls (live.com)
FL | E-bussen: De Lijn gaat volop voor groen - De Lijn
BXL& WL | Un nouveau pas à la STIB vers une décarbonisation complète des bus d’ici 2035, au TEC cela prendra un peu plus de temps - RTBF Actus
EU | Agreement on strong EU targets to reduce CO2 emissions (europa.eu)
Stock at end of year [Thousands]
Bus stock - BEV+PHEV [Thousands] | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
Public buses | 0.1 | 0.3 | 0.6 | 0.9 | 1.5 | 1.9 | 2.3 | 2.6 | 3 | 3.4 | 4 | 4.5 | 5.1 | 5.6 | 6 | 6.2
Private buses | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 0.6 | 0.8 | 0.9 | 1.1 | 1.2 | 1.4 | 1.5 | 1.7
Total | 0.1 | 0.3 | 0.6 | 0.9 | 1.5 | 2.1 | 2.6 | 3.1 | 3.6 | 4.2 | 4.9 | 5.6 | 6.3 | 7 | 7.5 | 7.9
Share of total stock [%] | 0.014691 | 1.876% | 3.606% | 5.46% | 9.318% | 12.46% | 15.67% | 18.89% | 22.1% | 25.31% | 29.62% | 33.93% | 38.23% | 42.54% | 45.63% | 47.78%
| Unit | Value
Usage (km/year) - public bus | km/year | 80000
Usage (km/year) - private bus | km/year | 28000
Efficiency - BEV (kWh/100km) | kWh/100km | 125
4
8
10
40
290
580

## 2.3. Building heat demand
2.3. Electrification of the heating sector
Residential
Key Drivers
Reduction in amount of new buildings 55k/y --> 40k/y based on allignemnt with Fluvius and most recent drop
Renovations increasing from 0.7% (1) towards 1.5% in 2036
FL: no more gas connections in new buildings from 2025: 96% HP, 4% District heating (2)
Other regions: 100% HP/DH in new built from 2035
Renovations & end-of-lifetime boiler replacement: 23% , 35% HP by 2030, 2035
Sources used
BE | Bouwvergunningen ¦ Statbel (fgov.be) (1)
FL | Aansluiting voor elektriciteit of aardgas ¦ Vlaanderen.be (2)
Current sales & stock
BE | ATTB, FRIXIS, Delta-EE, EHPA, Statista, EurObserv'ER, Fluvius
FL | VEKA: https://apps.energiesparen.be/energiekaart/vlaanderen/warmtepompen-aantal rapp-2021-18.pdf (vreg.be)
WL | bilan-domestique-et-equivalents-2019-v2.pdf (wallonie.be) p29
Building evolution | Unit | Value | Comment
New buildings | thousand/y | 41 | Alligned with Fluvius, this is a reduction compared to historical avg (55k/y)
Renovation rate avg 2024-2033 | % | 1%
Stock at end of year [Thousands]
Hydronic HP stock [Thousands] | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
HP Air-Water | 79 | 102 | 145 | 171 | 207 | 245 | 285 | 327 | 371 | 417 | 465 | 516 | 569 | 624 | 681 | 738
HP Ground-Water | 28 | 34 | 39 | 44 | 52 | 60 | 68 | 76 | 85 | 94 | 103 | 113 | 122 | 132 | 143 | 153
Total | 107 | 136 | 184 | 215 | 259 | 305 | 353 | 403 | 456 | 511 | 568 | 629 | 691 | 756 | 824 | 891
Stock at end of year [Thousands]
Aerothermal HP stock [Thousands] | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
HP Air-Air primary | 136 | 158 | 181 | 187 | 194 | 201 | 209 | 219 | 229 | 240 | 251 | 264 | 278 | 292 | 306 | 322
HP Air-Air secondary* | 546 | 632 | 725 | 736 | 747 | 759 | 773 | 788 | 804 | 821 | 840 | 860 | 881 | 903 | 923 | 943
Total | 682 | 790 | 906 | 923 | 941 | 960 | 982 | 1007 | 1033 | 1061 | 1091 | 1124 | 1159 | 1195 | 1229 | 1265
* Included in this category are Air-Air reversible heat pumps which have seen a sharp increase in recent years. These units are typically installed as an AC (cooling) unit but also have the capability to deliver heat, albeit in general limited to a part of the building and/or as a secondary form of heating
After consultation with ATTB, FRIXIS, Fluvius, UGeent and contacts within the heat pump sector, it was decided to categorise these A-A (reversible) units for 80% in the 'secondary'category as they will have different characteristics when it comes to yearly and hourly electricity demand
Consumption parameters | Unit | Value | Comment
Thermal space Heating demand - new build | kWh/y | 4400 | Fluvius
Thermal space Heating demand - renovated building | kWh/y | 8000 | Fluvius
Heat supplied by secondary heater | % of annual thermal heat | 20% | Alligned with Fluvius
Average Hot water demand | kWh/y | 1800 | Fluvius
Tertiary
Key Drivers
Business as usual in the evolution of new buildings - last 5y avg (1)
Renovations increasing from 0.7% (1) towards 1.5% in 2036
In general: faster uptake of Heat pumps as compared to residential sector
FL: no more gas connections in new buildings from 2025: 96% HP, 4% District heating (2)
Renovations: 100% HP by 2030
End-of-lifetime boiler replacement: 25% , 35% HP by 2030, 2035
Sources used
BE | Bouwvergunningen ¦ Statbel (fgov.be) (1)
FL | Verplichting elektrische warmtepomp bij nieuwbouw vervroegd naar 2025 - Ode (2)
Current sales & stock
BE | ATTB, FRIXIS, Delta-EE, EHPA, Statista, EurObserv'ER
FL | VEKA: https://apps.energiesparen.be/energiekaart/vlaanderen/warmtepompen-aantal rapp-2021-18.pdf (vreg.be)
FL | Verplichtingen voor niet-residentiële gebouwen ¦ Vlaanderen.be
WL | bilan-domestique-et-equivalents-2019-v2.pdf (wallonie.be) p29
Building evolution | Unit | Value
New buildings | thousand/y | 6.2
Renovation rate avg 2022-2035 | % | 1%
Stock at end of year [Thousands]
Hydronic HP stock [Thousands] | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
HP Air-Water | 1.6 | 2.2 | 3.1 | 8.8 | 15.3 | 22 | 30 | 39 | 47 | 57 | 68 | 79 | 90 | 102 | 115 | 129
HP Ground-Water | 1.3 | 1.5 | 1.8 | 2.9 | 4.4 | 6 | 7.8 | 9.6 | 11.4 | 13.5 | 15.6 | 17.9 | 20.3 | 22.9 | 25.7 | 28.5
Total | 2.9 | 3.7 | 4.9 | 11.7 | 19.7 | 28 | 37.8 | 48.6 | 58.4 | 70.5 | 83.6 | 96.9 | 110.3 | 124.9 | 140.7 | 157.5
Stock at end of year [Thousands]
Aerothermal HP stock [Thousands] | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
HP Air-Air primary | 9 | 12 | 13.8 | 14.5 | 15.6 | 16.7 | 18.2 | 20 | 22 | 24 | 26 | 29 | 32 | 35 | 38 | 41
HP Air-Air secondary* | 36 | 48 | 55 | 58 | 61 | 64 | 68 | 73 | 78 | 82 | 87 | 92 | 97 | 102 | 106 | 109
Total | 45 | 60 | 68.8 | 72.5 | 76.6 | 80.7 | 86.2 | 93 | 100 | 106 | 113 | 121 | 129 | 137 | 144 | 150
* Included in this category are Air-Air reversible heat pumps which have seen a sharp increase in recent years. These units are typically installed as an AC (cooling) unit but also have the capability to deliver heat, albeit in general limited to a part of the building and/or as a secondary form of heating
After consultation with ATTB, FRIXIS, Fluvius, UGeent and contacts within the heat pump sector, it was decided to categorise these A-A (reversible) units for 80% in the 'secondary'category as they will have different characteristics when it comes to yearly and hourly electricity demand
Consumption parameters | Unit | Value
Average Heating demand - new build | kWh/y | 17000
Average Heating demand - renovated building | kWh/y | 25500
Average Hot water demand | kWh/y | 3600

## 2.4 Industrial demand
2.4. Industrial demand
2.4.1. Additional electrification in industry & data centers
Our projections for Elia customers are informed by our load management exercise (LME), conducted yearly with our industrial customers
In 2024's exercise, customers defined several scenarios with an estimated probability.
These were then aligned in 3 different trajectories to account for diverse ways in which customers defined their scenarios (eg: inclusion of technical and economical key factors).
This tab gives the split per process for the trajectory suggested by Elia.
Total numbers are also given for a lower and higher trajectory.
Data from customers were collected up to the year 2033 (included). After that, Elia suggests to consider an extrapolation per process type, based on growth between 2030-2033.
Flexibility
It must be noted that a significant share of this additional electricity demand is flexible
Therefore, not all of this demand will result in additional peak demand and will likely be able to deliver flexibility services
Flexibility assumptions are presented in the tab "3.2 DSR industry"
Additional electrification in industry
Consolidated trajectories
TWh | Year | Electric ovens | Electric boiler | Heat pumps | Electric arc furnace | CCS/U | Data centers | Miscellaneous and inflexible processes | Total - proposed CENTRAL trajectory | LOW | HIGH
| 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2025 | 0.02 | 0.02 | 0 | 0.11 | 0 | 0.48 | 0.89 | 1.52 | 0.88 | 2.52
| 2026 | 0.11 | 0.15 | 0 | 0.22 | 0 | 0.73 | 1.57 | 2.78 | 1.85 | 4.39
| 2027 | 0.34 | 0.19 | 0.17 | 0.33 | 0 | 1.13 | 2.45 | 4.61 | 2.67 | 6.99
| 2028 | 0.43 | 0.33 | 0.42 | 0.76 | 0.05 | 1.42 | 3.26 | 6.67 | 3.34 | 12
| 2029 | 0.5 | 0.54 | 0.82 | 1.18 | 0.51 | 1.88 | 3.96 | 9.39 | 5.02 | 15.7
| 2030 | 1.12 | 0.58 | 1.23 | 2.68 | 0.77 | 2.26 | 5 | 13.64 | 6.44 | 20.07
| 2031 | 1.2 | 0.62 | 1.65 | 2.68 | 0.84 | 2.63 | 5.95 | 15.57 | 8.08 | 22.98
| 2032 | 1.24 | 0.7 | 2.23 | 2.68 | 1.05 | 3.01 | 7.19 | 18.1 | 11.5 | 30.02
| 2033 | 1.38 | 0.77 | 2.78 | 2.68 | 2.54 | 3.38 | 8.26 | 21.79 | 13.06 | 33.42
| 2034 | 1.46 | 0.83 | 3.06 | 2.68 | 3.12 | 3.76 | 8.97 | 23.88 | 14.38 | 34.54
| 2035 | 1.55 | 0.89 | 3.3 | 2.68 | 3.71 | 4.14 | 9.62 | 25.89 | 15.6 | 35.55
| 2036 | 1.64 | 0.96 | 3.68 | 2.68 | 4.3 | 4.51 | 10.45 | 28.22 | 17.12 | 36.87
*This excludes additional electricity demand from electrolyzers & other PtX processes

## 3.1 Storage
3.1 Pumped-storage, large scale storage and small scale home storage
In this section, pumped-storage, large scale batteries and small scale storage (home batteries) assumptions are detailed
3.1.1 Pumped-storage
The current installed capacity of pumped-storage in Belgium is based on the REMIT information regarding increased capacity of Coo and 144 MW of Platte-Taille. The reservoir volume integrates the extension work in Coo (2023, increasing the volume from 5213 to 5600 MWh). The turbining capacity in Coo is expected to reach 1161 MW with the installation of new turbines by end of 2026. Pumped-storage units are typically also used to provide ancillary services. Accordingly, in order to account for the provision of 'black-start' services, the total storage capacity available for economic dispatch in this analysis was decreased by 500 MWh.
Turbining capacity at the end of the mentioned year [MW]
|  |  | Today | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
| Turbining capacity | Total capacity | 1233 | 1281 | 1305 | 1305 | 1305 | 1305 | 1305 | 1305 | 1305 | 1305 | 1305 | 1305 | 1305
|  | Coo 1-6 | 1089 | 1137 | 1161 | 1161 | 1161 | 1161 | 1161 | 1161 | 1161 | 1161 | 1161 | 1161 | 1161
|  | Platte Taille 1-4 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144
Reservoir volume at the end of the mentioned year [MWh]
|  |  | Today | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
| Reservoir volume | Available storage for economic dispatch | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800
|  | Storage reservoir | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300
|  | Storage reservoir derating (black-start services) | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
3.1.2. Large scale batteries
Large-scale batteries are batteries which are usually directly connected to a DSO or TSO grid. These operate in a similar way to pumped-storage, in the sense that they can produce electricity and store it at opportune moments. They are therefore modelled in a similar way as pumped-storage (storage/production moments are optimised by the economic dispatch model), assuming they are in-the-market. Large-scale batteries are subject to the following constraints: maximum power, maximum energy storage, state of charge, charging/discharging efficiency. Two categories of capacity are considered - In service capacity based on total expected existing capacity at the end of 2024 and capacity already contracted in a CRM auction volume, including the 2024 auction results. - Additional potential capacity based on o all the projects in the ‘realisation phase’; o percentages of the projects in ‘connection study’ and ‘feasibility study’ phase; o extra additional potential, considering an extrapolation of the installation rate. The additional potential capacity could come based on projects known today at Elia. These projects will be consid-ered in the scenario if it is proven that they are economically viable without support mechanism. This will be deter-mined via the Economic Viability Assessment. The percentages of the projects assumed (33% of the ‘connection study’ projects and 15% of the ‘feasibility study’ projects) are based on expert view from all projects known by Elia. It takes into account several parameters in order to reflect realistic evolutions. The energy content of large-scale batteries is based on the information available for each project individually.
Capacity and volume of large scale storage at the end of the mentioned year [MW] or [MWh]
|  |  | Today | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
| Total potential capacity [MW] |  | 202 | 555 | 1157 | 1976 | 2420 | 3253 | 3592 | 3911 | 4230 | 4673 | 5116 | 5559 | 6002
| Capacity [MW] | Exisiting capacity | 202 | 431 | 431 | 955 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457
|  | Additional potential if economically viable | 0 | 124 | 726 | 1021 | 963 | 1796 | 2135 | 2454 | 2773 | 3216 | 3659 | 4102 | 4545
| Total potential volume [MWh] |  | 605 | 2028 | 4543 | 7792 | 9543 | 16241 | 18582 | 20845 | 23107 | 25369 | 27631 | 29894 | 32156
| Volume [MWh] | Existing volume | 605 | 1439 | 1439 | 3510 | 5419 | 5419 | 5419 | 5419 | 5419 | 5419 | 5419 | 5419 | 5419
| Reservoir volume [MWh] | Additional potential if economically viable | 0 | 589 | 3104 | 4282 | 4124 | 10822 | 13163 | 15426 | 17688 | 19950 | 22212 | 24475 | 26737
3.1.3. Small scale home batteries
The capacity of small-scale batteries is based on historic data from Fluvius and VEKA for Flanders. From 2019 to the 1st of April 2023, subsidies/bonus for home batterie have been put in place in Flanders. Around 19,000 premium were asked in 2021 in Flanders for home batteries. This volume increased to more than 33,000 in 2022 and 39,000 in 2023. For later years, the residential batteries for Flanders are aligned with regional assumptions, considering 200,000 units installed in 2030. For Wallonia and Brussels, as the installation of small-scale batteries is mostly driven by the installation of solar panels, an additional capacity equivalent to 0.3% of the total installed existing photovoltaic capacity is considered to be installed. The projection assumes battery of 4.5 kW in average with a duration of 2 hours in average (9 kWh). Small-scale batteries are mainly considered as "out-of-market" in the short-term but is assumed to evolve in the future towards a higher share of "in-the-market" batteries.
Capacity and volume of storage at the end of the mentioned year[MW] or [MWh]
|  |  | Today | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
| Capacity [MW] |  | 525 | 613 | 696 | 775 | 850 | 921 | 987 | 1054 | 1121 | 1190 | 1260 | 1330 | 1402
| Volume [MWh] |  | 1050 | 1226 | 1392 | 1550 | 1700 | 1842 | 1974 | 2108 | 2242 | 2380 | 2520 | 2660 | 2804

## 3.2. DSR industry
3.2. Demand Side Response in industry
In this section, demand-side response in industry is detailed
Existing DSR/market response volume per year
Proposal for existing market response starts from N-SIDE study (see WG adequacy on the 27th of August)
Potential follow methodology from AdeqFlex'23
Potential capacity at the end of the mentioned year [MW]
| 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
Total potential shedding capacity | 1732 | 1882 | 2032 | 2182 | 2332 | 2482 | 2632 | 2782 | 2932 | 3082 | 3232 | 3382 | 3532 | 3682
Existing DSR | 1732 | 1732 | 1732 | 1732 | 1732 | 1732 | 1732 | 1732 | 1732 | 1732 | 1732 | 1732 | 1732 | 1732
New potential DSR submitted to EVA - 25€/kW | 0 | 150 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
New potential DSR submitted to EVA - 50€/kW | 0 | 0 | 0 | 150 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
New potential DSR submitted to EVA - 75€/kW | 0 | 0 | 0 | 0 | 0 | 150 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
New potential DSR submitted to EVA - 100€/kW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 300 | 450 | 600 | 750 | 900 | 1050
Existing DSR - Details in shedding capacity | 1732* | 1732 | 1732 | 1732 | 1732 | 1732 | 1732 | 1732 | 1732 | 1732 | 1732 | 1732 | 1732 | 1732
Max use of 1 hour | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
Max use of 2 hours | 436 | 436 | 436 | 436 | 436 | 436 | 436 | 436 | 436 | 436 | 436 | 436 | 436 | 436
Max use of 4 hours* | 611 | 611 | 611 | 611 | 611 | 611 | 611 | 611 | 611 | 611 | 611 | 611 | 611 | 611
Max use of 8 hours | 374 | 374 | 374 | 374 | 374 | 374 | 374 | 374 | 374 | 374 | 374 | 374 | 374 | 374
No limit | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186
* The volume for ancillary services is included in the "max use of 4 hours" category
Flexibility from new large-scale loads
Just like the projection of demand from new large-scale loads, customers were asked to estimate future expected flexibility of their processes
Based on this, complemented with past research (carried out in the framework of AdeqFlex'23), flexibility % were updated
This percentage is applied on the installed power capacity, and allows to reduce demand in times of high prices
% of flexibility | 2026-36
Electric ovens | 80%
Electric boiler | 75%
Heat pumps | 40%
Electric arc furnace (EAF-DRI) | 75%
Carbon capture and storage | 0%
data centers | 20%
Miscellanous and other processes | 5%
1732
1050
1950
*1732 MW includes estimation from N-Side (1569 MW) – TJ volume (140 MW) + provision of balancing (303MW)
N-SIDE results was presented in WG adequacy on the 27th of August.
100 EUR/kW
75 EUR/kW
50 EUR/kW
25 EUR/kW
Potential given to the EVA
Existing DSR / market response

## 3.3. DSR end-user
3.3. Demand-Side Response end-user (residential and tertiary sector)
This sheet details the scenario information regarding the end-user flexibility in residential and tertiary sectors (electric vehicles, heat pumps and residential batteries). It shows the assupmtions regarding flexibility drivers, share of unlocked flexibility and profiles. More informaiton on the way the way electric vehicles, heat pumps and residential batteries are modelled can be found in Appendix D, E and F.
3.3.1 Flexibility drivers
Flexibility drivers give us a simple metric to approach how fast will flexibility penetrate the market.
Dynamic contracts are assumed to drive the growth of market flexibility (i.e.: dispatch an asset based on price signal).
Smart meters [Milions]
Smart meters are assumed to drive the growth of local flexibility (i.e.: dispatch an asset based on regional tariffs, or PV self-consumption).
The trajectory is aligned with the development plans of DSOs.
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
| Belgium | 3.98 | 4.38 | 4.78 | 5.18 | 5.58 | 5.98 | 6.24 | 6.48 | 6.52 | 6.55 | 6.58 | 6.58
| Flanders | 3.3 | 3.48 | 3.66 | 3.84 | 4.02 | 4.2 | 4.23 | 4.26 | 4.29 | 4.32 | 4.35 | 4.35
| Wallonia | 0.51 | 0.68 | 0.85 | 1.01 | 1.18 | 1.35 | 1.52 | 1.68 | 1.69 | 1.69 | 1.69 | 1.69
| Brussels | 0.17 | 0.22 | 0.27 | 0.33 | 0.38 | 0.43 | 0.49 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54
Dynamic contracts [thousands]
Dynamic contracts are assumed to drive the growth of market flexibility (i.e.: dispatch an asset based on price signal).
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
| Belgium | 10 | 20 | 50 | 90 | 160 | 270 | 430 | 590 | 750 | 870 | 960 | 1020
3.3.2 Share unlocked flex
These shares are based on flexibvility drivers as simple approximation, then applying a factor
EV per operation mode [thousands]
Only passenger cars & LDVs, in BEV equivalent (PHEV counted as half a BEV)
For V2 technology, first commercial model as of 2026
Elia suggests to consider 1% of new sales as V2-ready model in the local & market category,
ramping up to 5% of new sales in 2030
Evs [thousands]
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
| V0 - natural charging | 380 | 470 | 560 | 620 | 660 | 700 | 660 | 640 | 590 | 560 | 560 | 570
| V1H - local charging | 310 | 470 | 660 | 850 | 1060 | 1240 | 1370 | 1510 | 1680 | 1860 | 2030 | 2200
| V2H - vehicle-to-home | 0 | 0 | 10 | 10 | 20 | 30 | 40 | 40 | 50 | 60 | 70 | 80
| V1M - smart charging | 6 | 10 | 30 | 50 | 90 | 150 | 250 | 350 | 450 | 530 | 590 | 630
| V2M - vehicle-to-market | 0 | 0 | 0 | 1 | 3 | 6 | 11 | 16 | 21 | 26 | 29 | 31
HP per operation mode
Counting only heating needs equivalent heat pumps
Secondary Air-air HP accounted for as 20% of an equivalent HP
HPs [thousands]
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
| HP0 - natural heating | 530 | 570 | 610 | 640 | 680 | 720 | 750 | 790 | 820 | 860 | 910 | 970
| HP1H - local heating | 120 | 140 | 170 | 200 | 230 | 260 | 280 | 310 | 350 | 390 | 420 | 460
| HP1M - smart heating | 2 | 4 | 8 | 16 | 28 | 50 | 80 | 110 | 140 | 160 | 180 | 190
BATTERIES per operation mode
Residential batteries [thousands]
| Operation mode | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
| B2H - battery-to-home | 126 | 133 | 130 | 104 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| B2M - battery-to-market | 10 | 21 | 43 | 85 | 149 | 220 | 234 | 249 | 264 | 280 | 295 | 312
3.3.3 Profiles
This section give the hourly profile used for each asset, depending on its operating mode (natural, local flexibility or market flexibility).
Concerning local flexibility profiles:
- Local flexibility profiles has been developped to minimise consumer bill. This considers the price of energy and the regional tariffs (capacity tariff for Flanders, and Time of Use for Wallonia as of 2026).
- The profiles are also built on solar production, as PV self-consumption could drive dispatch of the assets.
- As this mean you could have a different profile for each day, for simplicity, illustrative profile for winter are presented here
Concerning market flexibility profiles, they are not presented here as these are output of the simulation (as described in the methodology appendices published with this excel)
3.3.3.1 Electric Vehicles (EV)
V0 - Natural charging
This profile assumes cars are charging as soon as they are plugged-in, whether at home, at work or at public charging stations.
Based on observations, Elia has developped work & public EV charging profile. These are based on 2023 data and combined in different proportions, based on littérature.
These proportions evolve in the years following the penetration of private EV in the EV market.
Share of profiles
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
home | 53.1% | 54.6% | 56.2% | 57.7% | 59.2% | 60.8% | 62.3% | 63.8% | 65.4% | 66.9% | 68.5% | 70%
work | 27.7% | 26.5% | 25.4% | 24.2% | 23.1% | 21.9% | 20.8% | 19.6% | 18.5% | 17.3% | 16.2% | 15%
public | 19.2% | 18.8% | 18.5% | 18.1% | 17.7% | 17.3% | 16.9% | 16.5% | 16.2% | 15.8% | 15.4% | 15%
V0 - Natural charging
|  | home | work | public | aggregate - 2026 | aggregate - 2036
| 0 | Residential batteries [thousands] 2025: 4.1%; Residential batteries [thousands] 2026: 1.3%; Residential batteries [thousands] 2027: 2.2%; Residential batteries [thousands] 2028: 3%; Residential batteries [thousands] 2029: 3.4%
| 1 | Residential batteries [thousands] 2025: 2.7%; Residential batteries [thousands] 2026: 0.5%; Residential batteries [thousands] 2027: 1.2%; Residential batteries [thousands] 2028: 1.8%; Residential batteries [thousands] 2029: 2.1%
| 2 | Residential batteries [thousands] 2025: 1.6%; Residential batteries [thousands] 2026: 0.4%; Residential batteries [thousands] 2027: 1%; Residential batteries [thousands] 2028: 1.2%; Residential batteries [thousands] 2029: 1.3%
| 3 | Residential batteries [thousands] 2025: 0.9%; Residential batteries [thousands] 2026: 0.3%; Residential batteries [thousands] 2027: 0.8%; Residential batteries [thousands] 2028: 0.7%; Residential batteries [thousands] 2029: 0.8%
| 4 | Residential batteries [thousands] 2025: 0.6%; Residential batteries [thousands] 2026: 0.2%; Residential batteries [thousands] 2027: 0.8%; Residential batteries [thousands] 2028: 0.5%; Residential batteries [thousands] 2029: 0.6%
| 5 | Residential batteries [thousands] 2025: 0.6%; Residential batteries [thousands] 2026: 0.2%; Residential batteries [thousands] 2027: 0.9%; Residential batteries [thousands] 2028: 0.5%; Residential batteries [thousands] 2029: 0.6%
| 6 | Residential batteries [thousands] 2025: 0.7%; Residential batteries [thousands] 2026: 0.2%; Residential batteries [thousands] 2027: 0.9%; Residential batteries [thousands] 2028: 0.6%; Residential batteries [thousands] 2029: 0.7%
| 7 | Residential batteries [thousands] 2025: 1.3%; Residential batteries [thousands] 2026: 1.3%; Residential batteries [thousands] 2027: 1.8%; Residential batteries [thousands] 2028: 1.4%; Residential batteries [thousands] 2029: 1.4%
| 8 | Residential batteries [thousands] 2025: 2.2%; Residential batteries [thousands] 2026: 7.1%; Residential batteries [thousands] 2027: 5.3%; Residential batteries [thousands] 2028: 4.1%; Residential batteries [thousands] 2029: 3.4%
| 9 | Residential batteries [thousands] 2025: 2.6%; Residential batteries [thousands] 2026: 16.3%; Residential batteries [thousands] 2027: 8.9%; Residential batteries [thousands] 2028: 7.4%; Residential batteries [thousands] 2029: 5.6%
| 10 | Residential batteries [thousands] 2025: 2.6%; Residential batteries [thousands] 2026: 16%; Residential batteries [thousands] 2027: 9.3%; Residential batteries [thousands] 2028: 7.4%; Residential batteries [thousands] 2029: 5.6%
| 11 | Residential batteries [thousands] 2025: 2.8%; Residential batteries [thousands] 2026: 12.8%; Residential batteries [thousands] 2027: 7.9%; Residential batteries [thousands] 2028: 6.4%; Residential batteries [thousands] 2029: 5.1%
| 12 | Residential batteries [thousands] 2025: 3%; Residential batteries [thousands] 2026: 9.1%; Residential batteries [thousands] 2027: 7.3%; Residential batteries [thousands] 2028: 5.4%; Residential batteries [thousands] 2029: 4.6%
| 13 | Residential batteries [thousands] 2025: 3%; Residential batteries [thousands] 2026: 6.8%; Residential batteries [thousands] 2027: 6.4%; Residential batteries [thousands] 2028: 4.6%; Residential batteries [thousands] 2029: 4.1%
| 14 | Residential batteries [thousands] 2025: 3.1%; Residential batteries [thousands] 2026: 6.5%; Residential batteries [thousands] 2027: 6.6%; Residential batteries [thousands] 2028: 4.7%; Residential batteries [thousands] 2029: 4.1%
| 15 | Residential batteries [thousands] 2025: 3.8%; Residential batteries [thousands] 2026: 4.8%; Residential batteries [thousands] 2027: 6.6%; Residential batteries [thousands] 2028: 4.6%; Residential batteries [thousands] 2029: 4.4%
| 16 | Residential batteries [thousands] 2025: 5.3%; Residential batteries [thousands] 2026: 3.9%; Residential batteries [thousands] 2027: 6.1%; Residential batteries [thousands] 2028: 5.1%; Residential batteries [thousands] 2029: 5.2%
| 17 | Residential batteries [thousands] 2025: 7.6%; Residential batteries [thousands] 2026: 2.4%; Residential batteries [thousands] 2027: 5.1%; Residential batteries [thousands] 2028: 5.7%; Residential batteries [thousands] 2029: 6.4%
| 18 | Residential batteries [thousands] 2025: 9.8%; Residential batteries [thousands] 2026: 1.5%; Residential batteries [thousands] 2027: 3.7%; Residential batteries [thousands] 2028: 6.5%; Residential batteries [thousands] 2029: 7.6%
| 19 | Residential batteries [thousands] 2025: 10.4%; Residential batteries [thousands] 2026: 1.5%; Residential batteries [thousands] 2027: 3.3%; Residential batteries [thousands] 2028: 6.7%; Residential batteries [thousands] 2029: 8%
| 20 | Residential batteries [thousands] 2025: 9.5%; Residential batteries [thousands] 2026: 1.5%; Residential batteries [thousands] 2027: 3.2%; Residential batteries [thousands] 2028: 6.2%; Residential batteries [thousands] 2029: 7.3%
| 21 | Residential batteries [thousands] 2025: 8.3%; Residential batteries [thousands] 2026: 1.4%; Residential batteries [thousands] 2027: 3.2%; Residential batteries [thousands] 2028: 5.5%; Residential batteries [thousands] 2029: 6.5%
| 22 | Residential batteries [thousands] 2025: 7.6%; Residential batteries [thousands] 2026: 1.4%; Residential batteries [thousands] 2027: 3.9%; Residential batteries [thousands] 2028: 5.3%; Residential batteries [thousands] 2029: 6.1%
| 23 | Residential batteries [thousands] 2025: 6.1%; Residential batteries [thousands] 2026: 1.4%; Residential batteries [thousands] 2027: 2.9%; Residential batteries [thousands] 2028: 4.2%; Residential batteries [thousands] 2029: 4.9%
V1H, V2H - local flexibility
V1H represents a local profile for smart charging. This means charging of an EV incentivised by regional tariff or PV self-consumption
V2H (or Vehicle-to-home) is similar but has the possibility to inject power to reduce local houseload
|  | V1H |  |  |  | V2H
|  | Capacity Tariff |  | Time of Use |  | Capacity Tariff |  | Time of Use
|  | With PV | Without PV | With PV | Without PV | With PV | Without PV | With PV | Without PV
| 0 | 4.3% | 5.5% | 3.1% | 4.3% | 4.2% | 5.8% | 2.8% | 3.6%
| 1 | 4.9% | 6.2% | 6.5% | 8.6% | 4.3% | 6.7% | 10.4% | 11.9%
| 2 | 5.4% | 6.8% | 10.1% | 12.9% | 4.4% | 7.3% | 18.2% | 20.6%
| 3 | 5.7% | 7.1% | 10.6% | 12.9% | 4.4% | 7.7% | 19.1% | 21.6%
| 4 | 5.6% | 7.1% | 10.6% | 12.7% | 4.4% | 7.8% | 19.3% | 21.9%
| 5 | 5.2% | 6.5% | 9.7% | 12% | 4.3% | 7.3% | 18.2% | 20.6%
| 6 | 4.4% | 5.5% | 6.1% | 7.8% | 4.1% | 6.4% | 10.4% | 11.9%
| 7 | 3.5% | 4.4% | 2.8% | 3.7% | 3.4% | 4.8% | 3.1% | 3.5%
| 8 | 3% | 3.5% | 0.3% | 0% | 3% | 3.6% | -2.7% | -4%
| 9 | 3.4% | 3.1% | 1.2% | 0% | 3.4% | 2.7% | -1% | -4.2%
| 10 | 4.3% | 2.8% | 3.3% | 1.2% | 4.8% | 2.5% | 2.5% | -0.7%
| 11 | 5.3% | 2.5% | 5.4% | 2.3% | 6.3% | 2.4% | 5.7% | 3%
| 12 | 5.9% | 2.4% | 6.7% | 3.5% | 7.2% | 2.4% | 7.9% | 6.7%
| 13 | 6% | 2.4% | 6.7% | 3.6% | 7.2% | 2.5% | 8% | 7%
| 14 | 5.2% | 2.6% | 6.2% | 4% | 6.2% | 2.6% | 7.6% | 7.2%
| 15 | 4.1% | 2.9% | 5.6% | 4.9% | 4.6% | 2.6% | 7% | 7.3%
| 16 | 3.1% | 3% | 3.4% | 3.6% | 3.1% | 2.5% | 3% | 3.1%
| 17 | 2.5% | 3% | 1.6% | 2% | 2.2% | 2.3% | -1.2% | -1.2%
| 18 | 2.4% | 3% | 0% | 0% | 2.1% | 2.3% | -5.1% | -5.3%
| 19 | 2.6% | 3.2% | 0% | 0% | 2.4% | 2.5% | -5.4% | -5.4%
| 20 | 2.9% | 3.6% | 0% | 0% | 2.8% | 3% | -5.2% | -5.2%
| 21 | 3.2% | 4% | 0% | 0% | 3.3% | 3.5% | -5% | -5%
| 22 | 3.4% | 4.3% | 0% | 0% | 3.7% | 4.1% | -4.7% | -4.7%
| 23 | 3.9% | 4.9% | 0% | 0% | 4% | 4.9% | -4.3% | -4.3%
3.3.3.2 Heat Pumps (HP)
HP0 - Natural heating
This profile is based on metered data of heating consumption
HP0 - natural heating
2026-36
| 0 | Residential batteries [thousands] 2025: 2.1%
| 1 | Residential batteries [thousands] 2025: 2.3%
| 2 | Residential batteries [thousands] 2025: 2.6%
| 3 | Residential batteries [thousands] 2025: 3.1%
| 4 | Residential batteries [thousands] 2025: 3.7%
| 5 | Residential batteries [thousands] 2025: 4.7%
| 6 | Residential batteries [thousands] 2025: 5.7%
| 7 | Residential batteries [thousands] 2025: 5.9%
| 8 | Residential batteries [thousands] 2025: 5.1%
9 | bar: Residential batteries [thousands] 2025
| 10 | Residential batteries [thousands] 2025: 3.5%
| 11 | Residential batteries [thousands] 2025: 3.4%
| 12 | Residential batteries [thousands] 2025: 3.5%
| 13 | Residential batteries [thousands] 2025: 3.6%
| 14 | Residential batteries [thousands] 2025: 3.9%
| 15 | Residential batteries [thousands] 2025: 4.7%
| 16 | Residential batteries [thousands] 2025: 5.5%
| 17 | Residential batteries [thousands] 2025: 5.8%
| 18 | Residential batteries [thousands] 2025: 5.7%
| 19 | Residential batteries [thousands] 2025: 5.6%
| 20 | Residential batteries [thousands] 2025: 5.3%
| 21 | Residential batteries [thousands] 2025: 4.5%
| 22 | Residential batteries [thousands] 2025: 3.4%
| 23 | Residential batteries [thousands] 2025: 2.4%
HP1H - local flexibility
HP1H represents a local profile for smart charging. This means charging of an EV incentivised by regional tariff or PV self-consumption
Flexibility from heat pumps has been limited as to not over-assume the flexibility that consumers would give (and impact their comfort, and overall heating needs).
Hence, it is assumed that 10% of daily neergy needs can be shifted at other time of the day
HP1H
|  | Capacity Tariff |  | Time of Use
|  | With PV | Without PV | With PV | Without PV
| 0 | Residential batteries [thousands] 2025: 3.3%; Residential batteries [thousands] 2026: 4%; Residential batteries [thousands] 2027: 2.9%; Residential batteries [thousands] 2028: 3%
| 1 | Residential batteries [thousands] 2025: 3.4%; Residential batteries [thousands] 2026: 4.1%; Residential batteries [thousands] 2027: 3.2%; Residential batteries [thousands] 2028: 3.5%
| 2 | Residential batteries [thousands] 2025: 3.7%; Residential batteries [thousands] 2026: 4.4%; Residential batteries [thousands] 2027: 3.7%; Residential batteries [thousands] 2028: 4.1%
| 3 | Residential batteries [thousands] 2025: 4.1%; Residential batteries [thousands] 2026: 4.8%; Residential batteries [thousands] 2027: 4.1%; Residential batteries [thousands] 2028: 4.5%
| 4 | Residential batteries [thousands] 2025: 4.7%; Residential batteries [thousands] 2026: 5.2%; Residential batteries [thousands] 2027: 4.7%; Residential batteries [thousands] 2028: 5.1%
| 5 | Residential batteries [thousands] 2025: 5.1%; Residential batteries [thousands] 2026: 5.5%; Residential batteries [thousands] 2027: 5.5%; Residential batteries [thousands] 2028: 5.9%
| 6 | Residential batteries [thousands] 2025: 5.3%; Residential batteries [thousands] 2026: 5.6%; Residential batteries [thousands] 2027: 6.1%; Residential batteries [thousands] 2028: 6.4%
| 7 | Residential batteries [thousands] 2025: 5.2%; Residential batteries [thousands] 2026: 5.3%; Residential batteries [thousands] 2027: 6.1%; Residential batteries [thousands] 2028: 6.3%
| 8 | Residential batteries [thousands] 2025: 5%; Residential batteries [thousands] 2026: 5%; Residential batteries [thousands] 2027: 5.6%; Residential batteries [thousands] 2028: 5.6%
| 9 | Residential batteries [thousands] 2025: 5%; Residential batteries [thousands] 2026: 4.8%; Residential batteries [thousands] 2027: 5.1%; Residential batteries [thousands] 2028: 5%
| 10 | Residential batteries [thousands] 2025: 5.3%; Residential batteries [thousands] 2026: 4.6%; Residential batteries [thousands] 2027: 5.2%; Residential batteries [thousands] 2028: 4.9%
| 11 | Residential batteries [thousands] 2025: 5.5%; Residential batteries [thousands] 2026: 4.5%; Residential batteries [thousands] 2027: 5.6%; Residential batteries [thousands] 2028: 5%
| 12 | Residential batteries [thousands] 2025: 5.7%; Residential batteries [thousands] 2026: 4.5%; Residential batteries [thousands] 2027: 5.9%; Residential batteries [thousands] 2028: 5.2%
| 13 | Residential batteries [thousands] 2025: 5.7%; Residential batteries [thousands] 2026: 4.6%; Residential batteries [thousands] 2027: 5.8%; Residential batteries [thousands] 2028: 5.2%
| 14 | Residential batteries [thousands] 2025: 5.6%; Residential batteries [thousands] 2026: 4.8%; Residential batteries [thousands] 2027: 5.7%; Residential batteries [thousands] 2028: 5.5%
| 15 | Residential batteries [thousands] 2025: 5.4%; Residential batteries [thousands] 2026: 4.7%; Residential batteries [thousands] 2027: 5.8%; Residential batteries [thousands] 2028: 5.8%
| 16 | Residential batteries [thousands] 2025: 4.9%; Residential batteries [thousands] 2026: 4.5%; Residential batteries [thousands] 2027: 5%; Residential batteries [thousands] 2028: 5.2%
| 17 | Residential batteries [thousands] 2025: 4.2%; Residential batteries [thousands] 2026: 4%; Residential batteries [thousands] 2027: 4.1%; Residential batteries [thousands] 2028: 4.3%
| 18 | Residential batteries [thousands] 2025: 3.6%; Residential batteries [thousands] 2026: 3.7%; Residential batteries [thousands] 2027: 3.2%; Residential batteries [thousands] 2028: 3.2%
| 19 | Residential batteries [thousands] 2025: 3.4%; Residential batteries [thousands] 2026: 3.6%; Residential batteries [thousands] 2027: 3.1%; Residential batteries [thousands] 2028: 3.1%
| 20 | Residential batteries [thousands] 2025: 3.6%; Residential batteries [thousands] 2026: 3.8%; Residential batteries [thousands] 2027: 2.9%; Residential batteries [thousands] 2028: 2.9%
| 21 | Residential batteries [thousands] 2025: 3.7%; Residential batteries [thousands] 2026: 4.1%; Residential batteries [thousands] 2027: 3%; Residential batteries [thousands] 2028: 3%
| 22 | Residential batteries [thousands] 2025: 3.7%; Residential batteries [thousands] 2026: 4.1%; Residential batteries [thousands] 2027: 2.9%; Residential batteries [thousands] 2028: 2.9%
| 23 | Residential batteries [thousands] 2025: 3.5%; Residential batteries [thousands] 2026: 4%; Residential batteries [thousands] 2027: 3.1%; Residential batteries [thousands] 2028: 3.1%
3.3.3.3 Residential Batteries
B2H - Batteries-to-home
B2H represents a smart dispatch of a battery based on regional tariff or PV self-consumption
B2H
|  | Capacity Tariff | Time of Use
|  | With PV | With PV
| 0 | Residential batteries [thousands] 2025: -1.2%; Residential batteries [thousands] 2026: -1.9%
| 1 | Residential batteries [thousands] 2025: -0.9%; Residential batteries [thousands] 2026: 0.5%
| 2 | Residential batteries [thousands] 2025: -0.8%; Residential batteries [thousands] 2026: 2.6%
| 3 | Residential batteries [thousands] 2025: -0.7%; Residential batteries [thousands] 2026: 2.6%
| 4 | Residential batteries [thousands] 2025: -0.7%; Residential batteries [thousands] 2026: 2.6%
| 5 | Residential batteries [thousands] 2025: -0.8%; Residential batteries [thousands] 2026: 2.6%
| 6 | Residential batteries [thousands] 2025: -0.9%; Residential batteries [thousands] 2026: 0.5%
| 7 | Residential batteries [thousands] 2025: -0.8%; Residential batteries [thousands] 2026: -1.4%
| 8 | Residential batteries [thousands] 2025: -0.3%; Residential batteries [thousands] 2026: -2.7%
| 9 | Residential batteries [thousands] 2025: 1%; Residential batteries [thousands] 2026: -1.1%
| 10 | Residential batteries [thousands] 2025: 2.5%; Residential batteries [thousands] 2026: 2.3%
| 11 | Residential batteries [thousands] 2025: 3.9%; Residential batteries [thousands] 2026: 5.4%
| 12 | Residential batteries [thousands] 2025: 4.6%; Residential batteries [thousands] 2026: 7.6%
| 13 | Residential batteries [thousands] 2025: 4.6%; Residential batteries [thousands] 2026: 7.6%
| 14 | Residential batteries [thousands] 2025: 3.7%; Residential batteries [thousands] 2026: 6.7%
| 15 | Residential batteries [thousands] 2025: 2.2%; Residential batteries [thousands] 2026: 5.2%
| 16 | Residential batteries [thousands] 2025: 0.4%; Residential batteries [thousands] 2026: 1.4%
| 17 | Residential batteries [thousands] 2025: -1.1%; Residential batteries [thousands] 2026: -2.1%
| 18 | Residential batteries [thousands] 2025: -1.9%; Residential batteries [thousands] 2026: -5.1%
| 19 | Residential batteries [thousands] 2025: -2.2%; Residential batteries [thousands] 2026: -5.4%
| 20 | Residential batteries [thousands] 2025: -2%; Residential batteries [thousands] 2026: -5.2%
| 21 | Residential batteries [thousands] 2025: -1.9%; Residential batteries [thousands] 2026: -5%
| 22 | Residential batteries [thousands] 2025: -1.7%; Residential batteries [thousands] 2026: -4.7%
| 23 | Residential batteries [thousands] 2025: -1.5%; Residential batteries [thousands] 2026: -4.3%
3.3.4 Availability of Evs (i.e. connection to a charger)
An electric vehicle can deliver flexibility only when connected to a charger
Based on 2023 metered data, and the Adeqflex'23 parameters, these availability profiles were developed. They account for home charging as well as work charging
No flexibility is assumed from public charging
This parameter is the basis of the power constraint for market flexibility of electric vehicles (V1M and V2M)
EV availability (for V1M & V2M)
|  | aggregate - 2026 | aggregate - 2036
| 0 | Residential batteries [thousands] 2025: 40.3%; Residential batteries [thousands] 2026: 47.6%
| 1 | Residential batteries [thousands] 2025: 40.3%; Residential batteries [thousands] 2026: 47.6%
| 2 | Residential batteries [thousands] 2025: 40.2%; Residential batteries [thousands] 2026: 47.5%
| 3 | Residential batteries [thousands] 2025: 40.1%; Residential batteries [thousands] 2026: 47.3%
| 4 | Residential batteries [thousands] 2025: 39.7%; Residential batteries [thousands] 2026: 46.9%
| 5 | Residential batteries [thousands] 2025: 38.6%; Residential batteries [thousands] 2026: 45.5%
| 6 | Residential batteries [thousands] 2025: 35%; Residential batteries [thousands] 2026: 40.9%
| 7 | Residential batteries [thousands] 2025: 29.5%; Residential batteries [thousands] 2026: 33.6%
| 8 | Residential batteries [thousands] 2025: 26.6%; Residential batteries [thousands] 2026: 28.5%
| 9 | Residential batteries [thousands] 2025: 25.5%; Residential batteries [thousands] 2026: 24.5%
| 10 | Residential batteries [thousands] 2025: 23.5%; Residential batteries [thousands] 2026: 21.5%
| 11 | Residential batteries [thousands] 2025: 21.6%; Residential batteries [thousands] 2026: 19.2%
| 12 | Residential batteries [thousands] 2025: 20.6%; Residential batteries [thousands] 2026: 18.2%
| 13 | Residential batteries [thousands] 2025: 20.2%; Residential batteries [thousands] 2026: 18%
| 14 | Residential batteries [thousands] 2025: 21.4%; Residential batteries [thousands] 2026: 19.6%
| 15 | Residential batteries [thousands] 2025: 23.3%; Residential batteries [thousands] 2026: 22.2%
| 16 | Residential batteries [thousands] 2025: 26.4%; Residential batteries [thousands] 2026: 26.6%
| 17 | Residential batteries [thousands] 2025: 28.5%; Residential batteries [thousands] 2026: 30.9%
| 18 | Residential batteries [thousands] 2025: 30.1%; Residential batteries [thousands] 2026: 34.8%
| 19 | Residential batteries [thousands] 2025: 33.5%; Residential batteries [thousands] 2026: 39.6%
| 20 | Residential batteries [thousands] 2025: 36.1%; Residential batteries [thousands] 2026: 42.9%
| 21 | Residential batteries [thousands] 2025: 37.9%; Residential batteries [thousands] 2026: 45%
| 22 | Residential batteries [thousands] 2025: 38.9%; Residential batteries [thousands] 2026: 46.2%
| 23 | Residential batteries [thousands] 2025: 39.4%; Residential batteries [thousands] 2026: 46.7%
*Electric Vehicles delivering flex only include passenger cars and Light Duty Vehicles
in BEV equivalent (counts PHEV as half a BEV)
*Secondary Air-air HP accounted for as 20% of an equivalent HP
illustrative example
illustrative example
illustrative example
illustrative example
illustrative example
illustrative example
illustrative example
illustrative example

## 3.4. Electrolysers
3.4. Electrolysers
This section presents the assumptions considered for electrolysers dedicated to green H2 production
Based on the following elements:
The ‘Vision and strategy Hydrogen’ (Oct. 22) aimed for 150 MW in 2025*.
By end-October 2024, there is 1 publicly planned project for electrolysers: Hyoffwind**, 25 MW.
For the CENTRAL scenario, it is proposed to keep 25 MW as total hydrogen electrolyser capacity for the studied horizon,
as long as no other concrete project is known.
Note that hydrogen electrolysers are assumed fully flexible, and dispatched when prices are low.
Their final consumption is an output of dispatch simulation.
Installed capacity at the end of the mentioned year [MW]
|  | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
| AdeqFlex'25 proposal | 0 | 0 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
SOURCE:
Hyoffwind as of 2026 ( source)
Hyoffwind, Belgium's first green hydrogen production plant: John Cockerill and BESIX confirmed as first-class industrial partners

## 4.1. Fuel and CO2 prices
4.1. Fuel and CO2 prices
Fuel and CO2 prices per year
The methodology applied to establish the prices between 2026 & 2036 is the following: - Average for the year 2024 has been established based on historical data (see the relevant source) - For all commodities, forward prices from contract were taken for the years before 2028 included on the 18/10/2024 (see the relevant source) - For the rest of the data, an interpolation was carried out between last computed price & the price forecasted by the WEO2024 in 2030, and between 2030. The scenario chosen is "Announced Pledges". - After 2030, values are interpolated between the WEO2024 forecast of 2030 & 2040 for fuel commodities. For CO2 prices, values are available for 2030, 2035 and 2040. - All prices are expressed in EUR24
Price in [€2024] | Years | [12 empty] | Sources |  |  | AREA | Comments
| 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | Historical average | Forward | Long term |  | Historical average (2024) | Forward (up to 2025) | Long term (until 2035)
Gas TTF [€/MWh] | 32.8242 | 38.5987 | 33.7779 | 28.5116 | 25.4229 | 22.3343 | 19.2457 | 18.9891 | 18.7325 | 18.4759 | 18.2193 | 17.9627 | 17.7061 | Dutch TTF Natural Gas Futures Historical Prices - Investing.com | Ice Endex TTF GAS (elexys.be) | World Energy Outlook 2022 – Analysis - IEA | EU |  | Consulted on the 18/10/2024 | Announced Pledges scenario taken from WEO
Coal ARA [€/MWh] | 14.5529 | 16.0173 | 14.5466 | 13.0758 | 11.6051 | 10.1343 | 8.6636 | 8.4876 | 8.3116 | 8.1357 | 7.9597 | 7.7837 | 7.6077 | Coal (API2) CIF ARA (ARGUS-McCloskey) Futures Quotes - CME Group | Coal (API2) CIF ARA (ARGUS-McCloskey) Futures Quotes - CME Group | World Energy Outlook 2022 – Analysis - IEA | EU |  | Consulted on the 18/10/2024 | Announced Pledges scenario taken from WEO
Oil [€/MWh] | 44.5291 | 37.7917 | 36.8447 | 36.3637 | 38.0991 | 39.8346 | 41.5701 | 41.0504 | 40.5308 | 40.0112 | 39.4916 | 38.9719 | 38.4523 | Crude Oil Overview - CME Group | Crude Oil Futures Quotes - CME Group | World Energy Outlook 2022 – Analysis - IEA | EU |  | Consulted on the 18/10/2024 | Announced Pledges scenario taken from WEO
CO2 EUA [€/tCO2] | 65.875 | 64.8271 | 66.8384 | 69.0204 | 88.3163 | 107.6123 | 126.9082 | 131.6085 | 136.3088 | 141.0091 | 145.7094 | 150.4097 | 153.2299 | EU Carbon Permits - Price - Chart - Historical Data - News (tradingeconomics.com) | Futures (eex.com) | World Energy Outlook 2022 – Analysis - IEA | EU |  | Consulted on the 18/10/2024 | Announced Pledges scenario taken from WEO
Legend: |  | Methodology:
Historical average
Forward prices |  |  | Historical average (for the year 2024)
WEO prices
Interpolation to WEO prices
Prices defined by forward contracts, as displayed on relevant source, consulted in October (18/10).
Interpolation between last forward price known & long-term price defined in WEO2022 for 2030 and 2040.
1
2
3
Proposal for gas price [€/MWh]
Proposal for carbon price [€/tCO2]
Proposal for Coal [€/MWh]
Proposal for Oil price [€/MWh]
1
3
2*
1
3
2*
1
3
2*
1
3
2*

## 4.2. Investment costs
4.2. Investment costs
This section gives an overview of assumptions related to investment costs used in the EVA
The first part presents the WACC and Hurdle Premium delivered by the Boudt study
The second part present all cost assumptions, and related sources, for FOM and CAPEX
All costs are expressed in euros beginning of 2024
The FOM values are based on the ENTRAS study on FOM and Blueprint studies.
The CAPEX values for all new thermal plants are aligned with the values chosen by the minister in the CRM 2024
The exception is made for the hydrogen fuelled CCGT and OCGT, for which the mean of Blueprint's values of 2030 and 2040 are used for the time window 2031-2035.
Blueprint’s values are used for the storage and renewable production assets.
All sources consulted in the framework of AdeqFlex23 have been added hereunder
| 2022 | 2023 | 2024* | Source
General Inflation | 10.35% | 1.01% | 1.03% | Bureau fédéral du Plan - Indice des prix à la consommation & prévisions d'inflation | *10/2023-10/2024
4.2.1 WACC and hurdle rate per technology
WACC & Hurdle Premium - Prof. Boudt
real WACC | 4.8%
Hurdle rate (WACC + hurdle premium)
Existing (assumed no extension costs) | CCGT | 7.7%
| OCGT | 7.7%
Existing (assuming extension costs needed) | CCGT | 9.3%
| OCGT | 10.3%
New | CCGT | 10.3%
| OCGT | 11.3%
| Demand response | 8.3%
| Batteries 2h | 8.3%
| Batteries 4h | 8.3%
RES | Wind onshore | 7.7%
| Wind offshore | 7.7%
| PV | 7.7%
4.2.2 CAPEX and FOM per technology and time horizon
All figures in EUR 2024
Technologies part of the structural block |  | Applies to | CAPEX [€/kW] |  | FOM (including major overhauls) [€/kW/y] | Construction period [years] | Investment economic lifetime [years] | Main Sources
|  |  | 2025-2030 | 2031-2036 | 2025-2036 | 2025-2036 | 2025-2036 | Source CAPEX | Source FOM
Existing (assumed no extension costs) | CCGT | Existing units <25 years | - | - | 36 | - | - |  | ENTRAS
| OCGT |  | - | - | 27 | - | -
| CHP | All existing capacity | - | - | 34 | - | -
| Turbojets | All existing capacity | - | - | 35 | - | - |  | AdeqFlex 2023 + inflation
| Demand Response | All existing capacity in 2024 | - | - | 12 | - | - |  | AdeqFlex 2023 + inflation
| Pumped Storage | All existing capacity | - | - | 30 | - | - |  | ENTRAS
Existing (assuming extension costs needed) | CCGT | Existing units >25 years | 120 |  | 31 | 0 | 15 | Blueprint study | ENTRAS
| OCGT |  | 100 |  | 29 | 0 | 15
New | CCGT | >800 MW | 840 |  | 31 | 3 | 20 | CRM 2024 | ENTRAS
|  | 400 < 800 MW | 1020 |  | 31 | 3 | 20
|  | < 400 MW | 1260 |  | 31 | 3 | 20
|  | H2 fueled >800W | - | 1120 | 38 | 3 | 20 | Blueprint study
| OCGT | >100 MW | 660 |  | 29 | 2 | 20 | CRM 2024
|  | <100 MW | 1200 |  | 29 | 2 | 20
|  | H2 fueled >100W | - | 900 | 33 | 2 | 20 | Blueprint study
| CHP | New capacity < 100 MW | 1200 |  | 35 | 2 | 20 | CRM 2024
| Demand response | New capacity 0 < 300 MW | All cost included in FOM |  | 25 | 0 | - |  | AdeqFlex 2023 + inflation
|  | New capacity 300 < 600 MW |  |  | 50 | 0 | -
|  | New capacity 600 < 900 MW |  |  | 75 | 0 | -
|  | New capacity 900 < 1200 MW |  |  | 100 | 0 | -
| Batteries/Storage | Large scale batteries (1h) | 320 | 300 | 26 | 1 | 15 | Blueprint study | ENTRAS
|  | Large scale batteries (2h) | 540 | 500 | 26 | 1 | 15
|  | Large scale batteries (4h) | 1010 | 910 | 26 | 1 | 15
| Pumped Storage - new unit | New unit | 2230 |  | 19 | 4 | 25 | Blueprint study | NREL
Renewables
RES | Wind onshore | New | 1290 | 1210 | 31 | 1 | 15 | Blueprint study | several sources (see dedicated section)
| Wind offshore | New (after 2 GW) | 2230 | 2100 | 60 | 3 | 15
| PV | New | 650 | 610 | 13 | 0 | 15
| Biomass | New | 2940 | 2860 | 96 | 3 | 20 |  | AdeqFlex 2023 + inflation
Sources:
AdeqFlex 2023 | Adequacy & flexibility study for Belgium (2024-2034) by Elia Group - Issuu
BluePrint study | Belgian electricity system blueprint for 2035-2050 by Elia Group - Issuu
ENTRAS study on FOM | 20231013 meeting
CRM 2024 - CAPEX selected by the minister | https://www.creg.be/fr/consultations-publiques/prd2820
NREL 2023 | Electricity Annual Technology Baseline (ATB) Data Download
RES: sources
TYNDP 2024 | Download ¦ ENTSOs TYNDP 2024 Scenarios
EC, 2021 | EU Reference Scenario 2020 - European Commission
RTE, 2021 | Futurs énergétiques 2050 : les chemins vers la neutralité carbone à horizon 2050 ¦ RTE
IEA-NEA, 2020 | Projected Costs of Generating Electricity 2020 – Analysis - IEA
UK GOV, 2023 | Electricity generation costs 2023 - GOV.UK
ENS, 2020 | Teknologikatalog for produktion af el og fjernvarme ¦ Energistyrelsen
Sources consulted in the framework of AdeqFlex'23:
Batteries: sources
https://www.elia.be/en/public-consultation/20220506_public-consultation-on-crm
Cost Projections for Utility-Scale Battery Storage: 2021 Update (nrel.gov)
DSM: sources
https://www.ademe.fr/sites/default/files/assets/documents/effacement-consommation-electrique-france_2017-synthese.pdf
https://www.cre.fr/content/download/21610/275050
Other Sources used
AFRY - peer review study presented to the TF CRM on 13/10/2022
PATHS2050 ¦ Energy outlook (energyville.be)
Lazard.com ¦ Levelized Cost Of Energy, Levelized Cost Of Storage, and Levelized Cost Of Hydrogen
World Energy Outlook 2022 (windows.net)
Renewable power generation costs in 2021 (irena.org)
EN2021_Fraunhofer-ISE_LCOE_Renewable_Energy_Technologies.pdf

## 4.3. Outages
4.3. Outages
4.3.1. Forced outage rates
Details around the calculation method can be found in the outage study report in annex of the public consultation report.
Category | Number of FO per year | Average FO rate [%] | Average duration of FO rate [hours]
Nuclear | 1.2 | 10%* | 576 hours [around 24 days]
CCGT | 9.4 | 6.7% | 117 hours [ around 5 days]
OCGT | 3.3 | 8.1% | 217 hours [around 9 days]
TJ | 3.4 | 10.1% | 126 hours [around 5 days]
CHP, waste, biomass | 3 | 6.2% | 120 hours [around 5 days]
Pumped Storage | 7 | 7.2% | 177 hours [around 7 days]
DC links | 1.8 | 6.1% | 212 hours [around 9 days]
*Nuclear FO rate of 10% as agreed with stakeholders during the public consultation of the CRM scenarios 2024
4.3.2. Planned outages
The latest public information (REMIT) regarding the planned outages will be used
For years were no data are available in REMIT, the data from ENTSO-E will be used : https://www.entsoe.eu/outlooks/midterm/

## 4.4. Flex. charact.
4.4. Flexibility characteristics
| Parameters | [8 empty] | Maximum upward flexibility |  |  | Maximim downward flexibility |  |  | Energy Limit | Clarification, justifications and remarks
Parameter | Minimum up time | Minimum down time | Hot start up time | Warm start up time | Cold start up time | Transition time from "hot" to "warm" | Transition time from "warm" to "cold" | Min Stable power | Ramp Rate | Ramping flexibility limit | Fast flexibility limit | Slow flexibility limit | Ramping flexibility limit | Fast flexibility limit | Slow flexibility limit
Definition | Duration that a unit needs to remain in "on" status after the start of an activation | Duration that a unit needs to remain in "off" status after the end of an activation | Duration between the activation signal and attaining minimum stable power in "hot", "warm" or "cold" conditions |  |  | Duration that a unit goes from "hot" to "warm" status after the end of an activation | Duration that a unit goes from "warm" to "cold" status after the end of an activation | Minimum power output level when in "on" status | Minimum power variation in a time period | Maximum share of the installed capacity which can participate in the categories upward ramping, fast and slow flex (without accounting other constraints, e.g. ramp rate) |  |  | Maximum share of the installed capacity which can participate in the categories downward ramping, fast and slow flex (without accounting other constraints, e.g. ramp rate) |  |  | expressed in number of hours during which the plant can product at its maximum capacity
Unit | hours | hours | hours | hours | hours | hours | hours | % Pmax | %Pmax/min | %Pmax | %Pmax | %Pmax | %Pmax | %Pmax | %Pmax | hours
Nuclear
Interconnections (AC & DC) | [9 empty] | ATC import -Pnom import |  |  | ATC export - Pnom export |  |  |  | Cross-border flexibility is constrained by the remaining import / export capacity after the day-ahead schedules. Additional constraints are implemented following :
*the availability of the cross-border energy service, particularly during high (> 300 €/MWh - reduced upward flexibility) / low price (< 0 €/MWh - reduced downward flexibility) periods
*estimations on balancing market liquidity on European balancing market platforms on aFRR and mFRR (by means of sensitivities)
*Ramping : 0 MW with sensitivities equal to 50 % aFRR needs
*Fast : 250 MW / 350 MW (= reserve sharing limits) with sensitivities equal to 50% mFRR needs
Renewable Generation
Wind offshore | [8 empty] | 100% |  |  |  | 65%Pnom | 65% Pnom | 65% Pom |  | Based on literature [1] and constrained based on day-ahead forecast errors (99th percentile of observed forecast errors).
Ramping flexibility limited to 400 MW and 925 MW of the installed offshore fleet (based on an installed capacity of 4.4 GW ) based on input stakeholders.
*This equals a share: *18% of current installed capacity ; and *21% of installed capacity (through the Princess Elisabeth Zone)
Wind onshore (only share CIPU) | [8 empty] | 100% |  |  |  |  | 90% Pnom | 90% Pnom |  | Based on literature [1] and further constrained based on day-ahead forecast errors (99th percentile of observed forecast errors).
Solar (only share CIPU) | [8 empty] | 100% |  |  |  |  | 90% Pnom | 90% Pnom |  | Based on return on experience, and analysis of day-ahead forecast errors
Run-of-River Hydro
Biofuel (only share CIPU) | 8h | 8h | 3h | 5h | 7h | 12h | 72h | 40% | 3% |  |  |  | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") |  | Based on literature [2] and CHP recent steam turbine values
CCGT
new | 2h | 2h | 1h | 1.5h | 2h | 8h | 48h | 30% | 11% | Pmax-Pnom (0% when "off") | Pmax-Pnom (0% when "off") | Pmax-Pnom (100% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") |  | Based on literature [3] and [4]
(to be commissioned)
recent | 3h | 3h | 1.5h | 2h | 3h | 8h | 48h | 40% | 6% | Pmax-Pnom (0% when "off") | Pmax-Pnom (0% when "off") | Pmax-Pnom (100% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off")
(commissioned after 2000)
old | 3h | 3h | 1.5h | 2,5h | 4h | 8h | 48h | 45% | 3% | Pmax-Pnom (0% when "off") | Pmax-Pnom (0% when "off") | Pmax-Pnom (100% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off")
(commissioned before 2000)
OCGT
new | 1h | 1h | 0.16h | 0.16h | 0.16h | 2h | 3h | 20% | 15% | Pmax-Pnom (0% when "off") | Pmax-Pnom (100% when "off") | Pmax-Pnom (100% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") |  | Based on literature [3] and [4]
existing | 1h | 1h | 0.16h | 0.16h | 0.16h | 2h | 3h | 30% | 12% | Pmax-Pnom (0% when "off") | Pmax-Pnom (100% when "off") | Pmax-Pnom (100% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off")
CHP
CHP (GAS TURBINE) | 4h | 4h | 1h | 1h | 4h | 2 h | 3 h | 50% | 10% |  |  |  | Pnom-Pmin | Pnom-Pmin | Pnom-Pmin | 8 hours | Based on literature [3] and CHP recent steam turbine values (+ [5] for energy limit) + input COGEN
CHP (CCGT) | 3h | 3h | 1h | 2h | 3h | 8h | 48h | 40% | 6% | Pmax-Pnom | Pmax-Pnom | Pmax-Pnom | Pnom-Pmin | Pnom-Pmin | Pnom-Pmin |  | Based on literature [3] and CHP recent steam turbine values (+ [5] for energy limit) + input COGEN
Large-scale storage
Pumped Storage | [8 empty] | 100% | Pmax- Pnom (0% when "off") | Pmax - Pnom | Pmax - Pnom | Pnom-Pmin (0% when "off") | Pnom - Pmin | Pnom - Pmin | 4,5 hours | Aggregation of PHS-sites. Based on literature review [6] and Elia's internal information *Pnom can be positive (power injections) or negative (power off-take) *Pmax is a positive value (maximum injection), Pmin is negative value (maximum offtake)
Large battery storage | [8 empty] | 100% | Pmax-Pnom | Pmax-Pnom | Pmax-Pnom | Pnom - Pmin | Pnom - Pmin | Pnom - Pmin | 1, 2 and 4 hours
Demand Side Response
Existing DSR | [8 empty] | 100% | 10% (Pmax-Pnom) | 40% (Pmax-Pnom) | Pmax - Pnom |  |  |  | 1, 2 , 4, 8 hours - no limit | Consistent with tab 3.2 DSR industry and and Elia's estimations [7] *Pnom is negative (power off-take) *Pmin is negative (maximum offtake), while Pmax is zero (maximum injection)
EV, HP and HB flexibility
1A. V1M Electric vehicles (uni-directional) | [8 empty] | 100% | 10% (Pmax-Pnom) | 10% (Pmax-Pnom) | 10% (Pmax-Pnom) | 10% (Pnom-Pmin) | 10% (Pnom-Pmin) | 10% (Pnom-Pmin) |  | Based on literature review [7;8;9] and Elia estimations *Pnom can be positive (power injections) or negative (power off-take) *Pmax has a positive value for HBs and V2M (maximum injection) *Pmax has a zero value for V1M and HPs (maximum injection) *Pmin is a negative value (maximum offtake) *Energy limit equals energy which can beactivated throughout the day (not in one stretch) *Pmax / Pmin are determined by limitations related to consumer comfort *The share of short-term flexible assets is set to 10% of the market flexible assets in adequacy simulations and assumed to increase to 40% towards 2036
1B. V2M Electric vehicles (bi-directional) | [8 empty] | 100% | 10% (Pmax-Pnom) | 10% (Pmax-Pnom) | 10% (Pmax-Pnom) | 10% (Pnom-Pmin) | 10% (Pnom-Pmin) | 10% (Pnom-Pmin)
2A. Heat Pumps - Sanitary Hot Water | [8 empty] | 100% | 10% (Pmax-Pnom) | 10% (Pmax-Pnom) | 10% (Pmax-Pnom) | 10% (Pnom-Pmin) | 10% (Pnom-Pmin) | 10% (Pnom-Pmin)
2B. Heat Pumps - Space Heating | [8 empty] | 100% | 10% (Pmax-Pnom) | 10% (Pmax-Pnom) | 10% (Pmax-Pnom) | 10% (Pnom-Pmin) | 10% (Pnom-Pmin) | 10% (Pnom-Pmin)
3. Home batteries | [8 empty] | 100% | 10% (Pmax-Pnom) | 10% (Pmax-Pnom) | 10% (Pmax-Pnom) | 10% (Pnom-Pmin) | 10% (Pnom-Pmin) | 10% (Pnom-Pmin) | 2 hours
Industrial flexibility
Electric arc furnace (EAF) | [8 empty] | 100% |  |  | Pmax - Pnom |  |  | Pnom - Pmin | no limit | Based on Elia's estimations *Pnom is negative (power off-take) *Pmin is negative (maximum offtake), while Pmax is zero (maximum injection) The flexible share of electric boilers and ovens have no energy limit (flexibility by a gas back-up alternative)
Electric boiler | [8 empty] | 100% | Pmax - Pnom | Pmax - Pnom | Pmax - Pnom | Pnom - Pmin | Pnom - Pmin | Pnom - Pmin | no limit
Electric oven | [8 empty] | 100% | Pmax - Pnom | Pmax - Pnom | Pmax - Pnom | Pnom - Pmin | Pnom - Pmin | Pnom - Pmin | no limit
Electrolyzers | [8 empty] | 100% |  | Pnom (0% when "off") | Pnom (0% when "off") |  |  |  |  | Based on literature [10]
Diesel + Turbojets | 0 h | 0.10 h | 0.05 h | 0.05 h | 0.05 h | 0 | 0 | 30% | 100% | Pmax-Pnom (0% when "off") | Pmax-Pnom (100% when "off") | Pmax-Pnom (100% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") |  | Based on Internal Combustion Engines [11]
Terminology
Pmax | Maximum injected power of the unit (MW)
Pnom | Day-Ahead Scheduled power of the unit (MW), i.e. positive or negative value
Pmin | Minimum stable power (MW) i.e positive value / Maximum absorbed power of the unit (MW) i.e negative value
ATCexport | Maximum available export capacity (MW)
ATCimport | Maximum available import capacity (MW)
ramping flex | Capacity which can be regulated continuously up- or downward in a timeframe of one minute
fast flex | Capacity which can be regulated up- or downward in a time frame of 15 minutes
slow flew | Capacity which can be regulated up- or downward in a time frame of 5 hours
List of references
1 | Van de vyver et al. | Comparison of wind turbine power control strategies to provide power reserves | [9 empty] | https://ieeexplore.ieee.org/abstract/document/7514034
2 | Dotzauer et al. | How to measure flexibility – Performance indicators for demand driven power generation from biogas plants | [9 empty] | https://www.sciencedirect.com/science/article/pii/S0960148118312059#sec3
3 | ENTSO-E | MAF Data | [9 empty] | https://www.entsoe.eu/Documents/SDC%20documents/MAF/MAF_2018_Dataset.xlsx
4 | Agora | Flexibility in thermal power plants, with a focus on existing coal-fired power plants | [9 empty] | https://www.agora-energiewende.de/fileadmin2/Projekte/2017/Flexibility_in_thermal_plants/115_flexibility-report-WEB.pdf
5 | Danish Energy Agency | Flexibility in the Power System - Danish and European experiences | [9 empty] | https://ens.dk/sites/ens.dk/files/Globalcooperation/flexibility_in_the_power_system_v23-lri.pdf
6 | Deloitte | Assessing the economic conditions of Belgian pumped-hydroelectric storage: comparative review of profitability drivers in Europe and evaluation of the current situation | [9 empty] | https://www.creg.be/sites/default/files/assets/Consult/2018/1718/RA1718-Annex2.7.pdf
7 | Gils, H. | Assessment of the theoretical demand response potential in Europe | [9 empty] | https://www.sciencedirect.com/science/article/abs/pii/S0360544214001534
8 | Le Baut et al. | Characterization of flexibility resources and distribution networks | [9 empty] | http://smartnet-project.eu/wp-content/uploads/2017/05/D1.2_20170522_V1.1.pdf
9 | Brouwer et al. | Least-cost options for integrating intermittent renewables in low-carbon power systems | [9 empty] | https://www.sciencedirect.com/science/article/abs/pii/S0306261915012167
10 | IRENA | Green Hydrogen Cost Reduction | [9 empty] | https://www.irena.org/publications/2020/Dec/Green-hydrogen-cost-reduction
11 | Wartisla | Reciprocating engines as a source reciprocating engines as a source of flexibility in a power system | [9 empty] | https://www.cire.pl/pliki/2/2018/13___niewinski.pdf

## 5.1. Flow based domains
5.1. Flow-based domains
This section concerns assumptions on flow-based domains. For more information on the methodology and assumptions, please refer to the online published study report.
5.1.1. Main parameters
Market Parameters |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | Comments
Flow-based perimeter |  | Central Europe CCR
Bidding zones |  | As Is | [11 empty] | ACER Decision No 11-2022 on the alternative bidding zone configurations only refers to assessment by next BZR study, so no official new configuration is known at this moment
minMACZT |  | See table below | [11 empty] | Perfect model assumption https://acer.europa.eu/Official_documents/Acts_of_the_Agency/Publications%20Annexes/ACER%20Report%20on%20the%20result%20of%20monitoring%20the%20MACZT%20Generic/ACER%20Report%20on%20the%20result%20of%20monitoring%20the%20MACZT%20Derogations.pdf
Treatment of external flows |  | Advanced Hybrid Coupling (AHC) | [11 empty] | Perfect model assumption
External & Allocation constraints |  | No Allocation constraints | [11 empty] | Perfect model assumption
Use of PST in capacity calculation |  | For Belgium: 1/2 For other: 1/3 | [11 empty] | All get a setpoint based on the nodal flow estimation (FE). In capacity calculation only the currently known PST’s are selected (BC). In capacity allocation none participate (MC)
Use of HVDC in flow-based capacity allocation |  | ALEGrO HVDC Piémond-Savoie |  | ALEGrO HVDC Piémond-Savoie Celtic Interconnector
5.1.2. MinRAM trajectories
Country |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | Justification
Austria | CORE borders | 59.68 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | Action plan 2021-2025
Belgium | CORE borders | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
Netherlands | CORE borders | 62.6 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | Action plan 2020-2025
Germany | CORE borders | 60.26 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | Action plan 2020-2025
France | CORE borders | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
Slovenia | CORE borders | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
Kroatia | CORE borders | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | Plans to adopt a action plan mid-2022
Romania | CORE borders | 62.6 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | Action plan 2021-2025
Czechia | CORE borders | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
Slovakia | CORE borders | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
Poland | CORE borders | 63.2 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | Action plan 2020-2025
Hungary | CORE borders | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
Ireland | CEC borders | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
Italy Nord | CEC borders | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70

## 6.1. Data for other countries
6.1. Data for other countries
The assumption for all European countries will be based on :
- ERAA 2024 - while preliminary data are publicly online available, final data are used here (Reaport to be published by end of the year by ENTSO-E)
- Bilateral exchanges with neighboring TSO's
- Completemented with latest policies/published studies
France
| Parameter | Units | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | Sources / Infos :
| Demand | Twh | 474 | 480 | 489 | 496 | 504 | 511 | 519 | 527 | 535 | 543 | 551 | 559 | Electricity demand based on central scenario from 'Bilan Prévisionnel' (September 2023). | Les bilans prévisionnels ¦ RTE (rte-france.com)
| Onshore Wind | GW | 25 | 26 | 28 | 29 | 30 | 32 | 33 | 35 | 36 | 37 | 39 | 40 | Onshore wind based on central scenario from 'Bilan Prévisionnel' (September 2023), in line with the historical installation rate. | Tableau de bord : éolien - Deuxième trimestre 2024 ¦ Données et études statistiques (developpement-durable.gouv.fr)
| Offshore Wind | GW | 2 | 3 | 3 | 3.6 | 3.6 | 3.9 | 4.4 | 6.1 | 12 | 15 | 18 | 21 | Offshore wind based on central scenario from 'Bilan Prévisionnel' (September 2023), in line with the 'Pacte éolien en mer' from the French governement. | 2022.03.14_pacte-eolien-mer.pdf (ecologie.gouv.fr)
| Solar | GW | 26 | 29 | 33 | 37 | 41 | 45 | 50 | 54 | 59 | 63 | 68 | 72 | Solar based on central scenario from 'Bilan Prévisionnel' (September 2023), in line with the historical installation rate. | Tableau de bord : solaire photovoltaïque - Deuxième trimestre 2024 ¦ Données et études statistiques (developpement-durable.gouv.fr)
| Gas | GW | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | Gas based on central scenario from 'Bilan Prévisionnel' (September 2023).
| Coal | GW | 1.1 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Coal based on central scenario from 'Bilan Prévisionnel' (September 2023) and on latest EDF publication on Cordemais. | Avenir du site de Cordemais : EDF envisage d’arrêter le projet « Ecocombust » et confirme sa volonté de maintenir sur le site une activité industrielle ¦ EDF FR
| Nuclear | GW | 61.8 | 61.8 | 61.8 | 61.8 | 61.8 | 61.8 | 61.8 | 61.8 | 61.8 | 61.8 | 61.8 | 61.8 | Nuclear based on the existing installed capacity and Flamanville 3 commissioning.
Germany
| Parameter | Units | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | Sources / Infos :
| Demand | Twh | 560 | 585 | 609 | 622 | 635 | 662 | 689 | 717 | 745 | 773 | 801 | 829 | Electricity demand based on ERAA24 | ERAA 2024 Call-for-Evidence on Preliminary Input Data - European Network of Transmission System Operators for Electricity - Citizen Space
| Onshore Wind | GW | 67 | 76 | 86 | 96 | 105 | 115 | 121 | 127 | 134 | 140 | 146 | 152 | Onshore wind based on ERAA24 interpolated towards 2030 target (confirmed in NECP Jun. 2024). After 2030, an extrapolation is done towards 2037 scenario B NEP 2025. | netzentwicklungsplan.de/sites/default/files/2024-07/Szenariorahmenentwurf_NEP2037_2025_1.pdf | https://commission.europa.eu/document/download/cd8ba2d6-1af6-4f37-aa07-059989bb1264_en?filename=GERMANY%E2%80%93FINAL_UPDATED_NECP_2021-2030_%28ENGLISH%29.pdf
| Offshore Wind | GW | 11 | 12 | 13 | 15 | 20 | 30 | 34 | 38 | 42 | 46 | 50 | 56 | Offshore wind based published (Jun. 24) development plans of offshore wind farms by BSH (part of Federal Ministry for Digital and Transport) - mostly in line with ERAA24 | BSH - Ongoing update of the site development plan
| Solar | GW | 115 | 135 | 155 | 175 | 195 | 215 | 234 | 252 | 271 | 289 | 308 | 326 | Solar based on ERAA24 interpolated towards 2030 target (confirmed in NECP Jun. 2024). After 2030, an extrapolation is done towards 2037 scenario B NEP 2025. | netzentwicklungsplan.de/sites/default/files/2024-07/Szenariorahmenentwurf_NEP2037_2025_1.pdf | https://commission.europa.eu/document/download/cd8ba2d6-1af6-4f37-aa07-059989bb1264_en?filename=GERMANY%E2%80%93FINAL_UPDATED_NECP_2021-2030_%28ENGLISH%29.pdf | https://commission.europa.eu/document/download/cd8ba2d6-1af6-4f37-aa07-059989bb1264_en?filename=GERMANY%E2%80%93FINAL_UPDATED_NECP_2021-2030_%28ENGLISH%29.pdf
| Gas | GW | 26 | 25.8 | 24.9 | 24.8 | 27.2 | 27.2 | 27.2 | 27.2 | 27.2 | 27.2 | 27.2 | 27.2 | Gas based on ERAA24 until 2029 and kept constant after - the exact amount will be calculated respecting security of supply criteria and EVA. | ERAA 2024 Call-for-Evidence on Preliminary Input Data - European Network of Transmission System Operators for Electricity - Citizen Space
| Coal | GW | 22.5 | 22.2 | 21.2 | 19.5 | 15.9 | 12.9 | 11.8 | 9.4 | 7.8 | 5 | 3.2 | 3.1 | Coal based on ERAA24, in line with coal phase-out by 2038 | ERAA 2024 Call-for-Evidence on Preliminary Input Data - European Network of Transmission System Operators for Electricity - Citizen Space
| Nuclear | GW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Nuclear based on ERAA24, in line with nuclear phase-out in 2023. | ERAA 2024 Call-for-Evidence on Preliminary Input Data - European Network of Transmission System Operators for Electricity - Citizen Space
Netherlands
| Parameter | Units | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | Sources / Infos :
| Demand | Twh | 129 | 134 | 138 | 143 | 148 | 153 | 160 | 168 | 176 | 183 | 191 | 198 | Electricity demand based on ERAA24 | ERAA 2024 Call-for-Evidence on Preliminary Input Data - European Network of Transmission System Operators for Electricity - Citizen Space
| Onshore Wind | GW | 7.7 | 8 | 8.4 | 8.8 | 9.1 | 9.4 | 9.7 | 10 | 10.3 | 10.6 | 10.9 | 11.2 | Onshore wind based on Monitoring leveringszekerheid (TenneT, 2024) | tennet-drupal.s3.eu-central-1.amazonaws.com/default/2024-05/20240514 Monitor Leveringszekerheid 2024_0.pdf
| Offshore Wind | GW | 4.9 | 5.6 | 6.4 | 6.4 | 10.4 | 12.4 | 16.4 | 20.4 | 21.1 | 21.8 | 22.5 | 23.2 | Offshore wind based on Routekaart wind op zee (April 2024) | https://open.overheid.nl/documenten/a5b91671-5b23-45b5-aa0b-72439730a4dc/file
| Solar | GW | 26 | 27 | 29 | 31 | 33 | 35 | 37 | 39 | 41 | 43 | 45 | 47 | Onshore wind based on Monitoring leveringszekerheid (TenneT, 2024) | tennet-drupal.s3.eu-central-1.amazonaws.com/default/2024-05/20240514 Monitor Leveringszekerheid 2024_0.pdf
| Gas | GW | 13 | 12 | 12 | 11 | 10 | 9.2 | 9.2 | 8.9 | 8.9 | 6.2 | 5.2 | 4.9 | Gas capacity based on ERAA24 - the exact amount will be calculated respecting security of supply criteria and EVA. | ERAA 2024 Call-for-Evidence on Preliminary Input Data - European Network of Transmission System Operators for Electricity - Citizen Space
| Coal | GW | 2.7 | 2.7 | 2.7 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Coal capacity based on ERAA24 | ERAA 2024 Call-for-Evidence on Preliminary Input Data - European Network of Transmission System Operators for Electricity - Citizen Space
| Nuclear | GW | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.49 | 0.49 | 0 | 0 | 0 | Nuclear capacity based on ERAA24 | ERAA 2024 Call-for-Evidence on Preliminary Input Data - European Network of Transmission System Operators for Electricity - Citizen Space
United Kingdom
| Parameter | Units | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | Sources / Infos :
| Demand | Twh | 286 | 291 | 296 | 304 | 314 | 328 | 342 | 360 | 383 | 405 | 425 | 451 | Electricity demand based on 'Electric Engagement' scenario from 'Future Energy Scenarios' (July 2024). | Future Energy Scenarios (FES) ¦ National Energy System Operator (neso.energy)
| Onshore Wind | GW | 17 | 19 | 21 | 24 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | Onshore wind based on 'Electric Engagement' scenario from 'Future Energy Scenarios' (July 2024).
| Offshore Wind | GW | 23 | 27 | 29 | 37 | 46 | 54 | 59 | 63 | 72 | 77 | 83 | 91 | Offshore wind based on 'Electric Engagement' scenario from 'Future Energy Scenarios' (July 2024).
| Solar | GW | 22 | 25 | 28 | 31 | 34 | 36 | 39 | 43 | 46 | 49 | 51 | 54 | Solar based on 'Electric Engagement' scenario from 'Future Energy Scenarios' (July 2024).
| Gas | GW | 43 | 43 | 44 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | Gas based on 'Electric Engagement' scenario from 'Future Energy Scenarios' (July 2024) until 2029 an kept constant after - the exact amount will be calculated respecting security of supply criteria and EVA.
| Coal | GW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Coal phase-out by end of 2023.
| Nuclear | GW | 6 | 3.6 | 3.6 | 1.2 | 1.2 | 4.4 | 4.4 | 4.4 | 7.6 | 7.6 | 7.6 | 9.3 | Unit-by-unit analysis | https://www.edfenergy.com/media-centre/investment-boost-maintain-uk-nuclear-output-current-levels-until-least-2026 | https://www.edf.fr/groupe-edf/espaces-dedies/journalistes/tous-les-communiques-de-presse/point-dactualite-sur-le-projet-hinkley-point-c
Spain
| Parameter | Units | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | Sources / Infos :
| Demand | Twh | 242 | 249 | 255 | 259 | 265 | 270 | 278 | 280 | 279 | 283 | 285 | 287 | Electricity demand based on ERAA24 | ERAA 2024 Call-for-Evidence on Preliminary Input Data - European Network of Transmission System Operators for Electricity - Citizen Space
| Onshore Wind | GW | 36 | 39 | 42 | 46 | 50 | 54 | 57 | 61 | 65 | 68 | 72 | 75 | Onshore wind based on ERAA24 | ERAA 2024 Call-for-Evidence on Preliminary Input Data - European Network of Transmission System Operators for Electricity - Citizen Space
| Offshore Wind | GW | 0 | 0 | 0.1 | 0.3 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | Offshore wind based on ERAA24 | ERAA 2024 Call-for-Evidence on Preliminary Input Data - European Network of Transmission System Operators for Electricity - Citizen Space
| Solar | GW | 43 | 50 | 55 | 59 | 64 | 73 | 81 | 90 | 98 | 108 | 117 | 126 | Solar based on ERAA24 | ERAA 2024 Call-for-Evidence on Preliminary Input Data - European Network of Transmission System Operators for Electricity - Citizen Space
| Gas | GW | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 126 | Gas capacity based on ERAA24 - the exact amount will be calculated respecting security of supply criteria and EVA. | ERAA 2024 Call-for-Evidence on Preliminary Input Data - European Network of Transmission System Operators for Electricity - Citizen Space
| Coal | GW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Coal capacity based on ERAA24 | ERAA 2024 Call-for-Evidence on Preliminary Input Data - European Network of Transmission System Operators for Electricity - Citizen Space
| Nuclear | GW | 7.1 | 7.1 | 6.1 | 5.1 | 5.1 | 3 | 3 | 2.1 | 2.1 | 2.1 | 0 | 0 | Nuclear capacity based on ERAA24 | ERAA 2024 Call-for-Evidence on Preliminary Input Data - European Network of Transmission System Operators for Electricity - Citizen Space
Italy
| Parameter | Units | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | Sources / Infos :
| Demand | Twh | 322 | 327 | 333 | 339 | 345 | 349 | 354 | 358 | 363 | 367 | 372 | 376 | Electricity demand based on ERAA24 | ERAA 2024 Call-for-Evidence on Preliminary Input Data - European Network of Transmission System Operators for Electricity - Citizen Space
| Onshore Wind | GW | 18 | 20 | 22 | 24 | 26 | 27 | 27 | 28 | 29 | 29 | 30 | 31 | Onshore wind based on Documento di Descrizione degli Scenari 2024 | Documento di Descrizione degli Scenari 2024
| Offshore Wind | GW | 0 | 0 | 0 | 0 | 2.1 | 2.9 | 3.8 | 4.6 | 5.4 | 6.2 | 7 | 7.8 | Offshore wind based on Documento di Descrizione degli Scenari 2024 | Documento di Descrizione degli Scenari 2024
| Solar | GW | 50 | 58 | 65 | 72 | 79 | 82 | 86 | 89 | 93 | 96 | 99 | 103 | Solar based on Documento di Descrizione degli Scenari 2024 | Documento di Descrizione degli Scenari 2024
| Gas | GW | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | Gas capacity based on ERAA24 - the exact amount will be calculated respecting security of supply criteria and EVA. | ERAA 2024 Call-for-Evidence on Preliminary Input Data - European Network of Transmission System Operators for Electricity - Citizen Space
| Coal | GW | 1.3 | 0.3 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Coal capacity based on ERAA24 | ERAA 2024 Call-for-Evidence on Preliminary Input Data - European Network of Transmission System Operators for Electricity - Citizen Space
| Nuclear | GW | / | / | / | / | / | / | / | / | / | / | / | / | Nuclear capacity based on ERAA24 | ERAA 2024 Call-for-Evidence on Preliminary Input Data - European Network of Transmission System Operators for Electricity - Citizen Space
Poland
| Parameter | Units | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | Sources / Infos :
| Demand | Twh | 168 | 172 | 175 | 179 | 183 | 187 | 190 | 194 | 197 | 199 | 203 | 206 | Electricity demand based on ERAA24 | ERAA 2024 Call-for-Evidence on Preliminary Input Data - European Network of Transmission System Operators for Electricity - Citizen Space
| Onshore Wind | GW | 11.5 | 12.1 | 12.7 | 13.3 | 13.9 | 148 | 15.6 | 16.4 | 16.7 | 16.9 | 17.2 | 17.5 | Onshore wind based on ERAA24 until 2034, extrapolated until 2036 | ERAA 2024 Call-for-Evidence on Preliminary Input Data - European Network of Transmission System Operators for Electricity - Citizen Space
| Offshore Wind | GW | 1.9 | 4 | 6 | 6.8 | 7.6 | 8.2 | 8.9 | 9.6 | 10.2 | 10.9 | 11.5 | 12.2 | Offshore wind based on ERAA24 until 2034, extrapolated until 2036 (interpolated for missing years in ERAA24) | ERAA 2024 Call-for-Evidence on Preliminary Input Data - European Network of Transmission System Operators for Electricity - Citizen Space
| Solar | GW | 20.41 | 22.06 | 23.7 | 25.35 | 27 | 28.8 | 30.6 | 32.4 | 34.2 | 36 | 37.8 | 39.6 | Onshore wind based on ERAA24 until 2034, extrapolated until 2036 | ERAA 2024 Call-for-Evidence on Preliminary Input Data - European Network of Transmission System Operators for Electricity - Citizen Space
| Gas | GW | 6.7 | 7.5 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | Gas capacity based on ERAA24 until 2029 an kept constant after - the exact amount will be calculated respecting security of supply criteria and EVA. | ERAA 2024 Call-for-Evidence on Preliminary Input Data - European Network of Transmission System Operators for Electricity - Citizen Space
| Coal | GW | 20 | 20 | 20 | 19 | 19 | 16 | 15 | 14 | 14 | 12 | 8.2 | 6.2 | Coal capacity based on ERAA24 | ERAA 2024 Call-for-Evidence on Preliminary Input Data - European Network of Transmission System Operators for Electricity - Citizen Space
| Nuclear | GW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | New nuclear units assumed beyond the timehorizon of this study |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0